CAN1101[FW28_PN01_16SBY03_211117]

The addition of automatic charging activation requires that the "automatic charging activation" function is set to be enabled by the host computer. Once this function is switched on, the following changes will occur.

1、No more shutdown after under-voltage protection, only when the minimum cell voltage is less than or equal to the "cell low voltage no-charge" setting will the shutdown be executed.

2. After under-voltage protection or residual capacity protection, wait for the "charge activation interval" setting time to arrive and force the output for 60 seconds to activate the charger.

3. Step 2 is repeated in one delay until the minimum cell voltage is less than or equal to the "cell low voltage no-charge" setting, after which the charging can only be activated manually by pressing the button.

4. When the "Auto-activate charging" function is switched on, the "Low-voltage charge ban" function will not work, otherwise there will be a conflict.

5、Manually forced output undervoltage protection and low voltage battery cell prohibition, key release

6、After under-voltage protection or remaining capacity protection, the corresponding number of charge activation times will be activated automatically, the number of charge activation times can be set

7、Standby hibernation shutdown, charge and discharge current maintain more than 5S clear time re-record.

8. Only 30 seconds have been changed. 5 seconds will be cut off when more than 3A current is detected after automatic activation. 5 seconds delay is also available when the standby state is interrupted by charging and discharging current.

9. Maximum number of automatic activations set to 30

10. The maintenance time for "automatic charge activation" is adjusted to 1 minute and 60 seconds.

11. The upper limit for the "number of charge activations" setting has been adjusted from 30 to 100.

12. blocking the "standby switch-off function" during "automatic charging activation".

Brief description.

1、No more shutdown after under voltage protection and remaining capacity protection, wait for the "charge activation interval" setting time to arrive and automatically resume output for 60 seconds to the charger

2、Under-voltage protection and residual capacity protection automatic recovery times reached, BMS shutdown

3、After the under-voltage protection and residual capacity protection are automatically restored, the BMS will shut down if the battery is discharged to a "low voltage cell prohibition".

4、Manually enforced output under voltage protection and low voltage battery cell prohibition charging, key release

[CAN1101[FW29_HW14_PN01_220524].hex] Modification Notes

i. Increased charging overvoltage protection to prevent damage to the current limiting section when switching to active or passive current limiting at high currents.

II. Discharge reversal to release charging protection, e.g. how to turn on the charging switch when discharging while waiting for intermittent replenishment; ***V28_SD shield

1. Discharge reversal lift from "Discharge - above 3A for 1 second" to "Discharge - above 10A for 10 seconds", buffering the BMS charge protection inverter regulation

The effect of discharge currents from the process.

2. Intermittent charge waiting is changed from "Charge capacity down to 0 and switch off" to "Charge capacity down to 0 and switch on only";

III. "ID35A_Byte7_bit[3:2]" in "VIC & SMA" CAN3 protocol changed from 01=Alarm not triggered to 00=No change retained

"(Resolving reserved alarms for SMA inverters used by Shunden overseas customers)

35A_Byte7_bit[3:2]: victron =System status[Onlie/offline]

SMA =Reversed

Fourth, the discharge request current is modified from 0.5C to 1C (to solve the request made by Shuangdeng's overseas customers using DEY inverters)

1. Discharge request current changes in Pai Energy Protocol 351.

2. alteration of the discharge request current in Gurvat 311.

3. The change in charge request current is buffered by adding a buffer step of the number of battery units with charging capacity * 1A per second;

V. Addition of ID_314_320_322 to the "Growalt " CAN2 protocol, compatible with Guravat SPH inverters; ***V28_SD shield

VI. Frequent recording of historical data (frequent recording when the Victron inverter is connected to standby)

Problem: Historical data are frequently recorded on some occasions when batteries are floating, especially when the load current is close to the effective discharge current.

Modified: The history trigger condition is changed from "active charging, active discharging or standby state switching" to "charging above 3A, discharging above 3A or waiting state

Switching" before recording.

[CAN1101[FW28_HW14_PN01_220526_SD].hex] Version Modification Notes

I. The charge request current is 0.5C, and the discharge request current for multiple parallel groups is "changed from 0.5C to 1.0C" according to the customer's request;

II. "VIC & SMA" CAN3 protocol ID35A_Byte7_bit[3:2] "changed from 01=alarm not triggered to 00=no change reserved";

[CAN1101[FW29_HW14_PN01_220528].hex] Version Modification Notes

I. "Growalt " Addition of ID_314_320_322 to the CAN2 protocol.

II. "Discharge - 10A or more for 10 seconds" enables the charging protection to be lifted in the reverse direction and the charging MOS no longer switched off when waiting for intermittent replenishment.

CAN1101[FW29_HW14_PN01_220623.ehex]

1. ID 320: change to "GT", maiden voyage 35F version: 1429 plus software version.