
 MODBUS RTU三相储能通信规约
（版权所有，翻版必究）
更改记录

	版本号
	更改内容
	责任人
	更改日期

	V100
	初始版
	刘胜利
	2020.09.16

	
	
	
	

	V103
	增加DeyePack电池协议500开始
	刘胜利
	2021.07.01

	V104
	增加交流测数据寄存器为32bit，原先寄存器作为数据低16位. 687-709号寄存器
	刘胜利
	2021.11.22

	
	增加电网标准需要的寄存器
	陈旭东
	2021.12.22

	V105
	.1  增加customized register
	  陈旭东
	2023.10.06

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


概述

本协议适用于我司三相储能逆变器与上位机监控和DSP之间的通信协议。采用MODBUS RTU通讯规约。本协议可以实时读取逆变器的运行信息和对逆变器控制操作。

物理接口

采用RS485/RS232，为异步收发方式，主从模式，固定波特率。

----波特率：9600bps

----奇偶校验位：None

----数据位：8

----停止位：1

帧间间隔时间要求

数据帧格式

	Slave Address
	Function code
	Data
	CRC Check

	8-Bits
	8-Bits
	Nx8-Bits
	16-Bits


Slave Address域：是对应的从机地址，必须和逆变器的从机地址匹配。

Function code域：功能码，目前只开放03H、10H功能码。

	Function code(Hex)
	中文名
	寄存器地址
	功能

	02H
	读开关输入状态
	
	读故障信息寄存器内容

	03H
	读保持寄存器
	0~59/500~2000
	读设置寄存器内容

	04H
	读输入寄存器
	
	读逆变器信息内容

	05H
	写单个线圈
	
	开关机设置功能

	06H
	写单个保持寄存器
	
	设置单字节功能

	10H
	写多个保持寄存器
	60-499
	设置多字节功能


Data域：包括起始寄存器地址，数据长度，数据字节个数，数据内容。都是高字节在前，低字节在后。

CRC Check域： CRC查表校验方式，低字节在前高字节在后。

错误信息及数据的处理
从机回复(16进制)： 
	Slave Address
	Function code
	Error code
	CRC Check

	xx
	xx|0x80
	xx
	低字节
	高字节

	
	
	
	xx
	xx


逆变器通讯模块检测到除了CRC 码出错以外的错误时，必须向主机回送信息，功能码的最高位置为1，即在主机发送的功能码的基础上加128 。

逆变器通讯模块响应回送的错误码：
0x01 非法的功能码 服务器不了解功能码
0x02 非法的数据地址 与请求有关
0x03 非法的数据值 与请求有关
0x04服务故障 逆变器通讯模块在执行过程中无法取出数据故障
详细协议描述

0-59寄存器地址为可读寄存器类型， 0x03功能码。

60-499寄存器地址为可读写寄存器类型， 0x10功能码。

500-2000寄存器地址为可读寄存器类型， 0x03功能码。

03读固有属性区，对应功能码0x03,地址范围0~59

	Addr
	Register meaning
	R/W
	data range
	unit
	note

	

	000
	设备类型

Device type
	R
	
	
	0X0200  组串机 inverter

0X0300  单相储能机 hybird

0X0400  微逆机MI microinverter

0X0500  低压三相储能机 phase3 hybird

0X0600  高压三相储能机

         0600   三相高压6-15kw

         0601   三相高压20-50kw 

	001
	Modbus address
	R
	[1,247]
	
	

	002
	通讯协议版本Communication protocol version
	R
	‘0’~’9’; ‘A’~’Z’
	
	固件所遵从的本协议的版本，如 0x 0102 代表 1.2 版

	003
	SN byte 01
	R
	‘0’~’9’; ‘A’~’Z’
	
	The serial number is ten ASCII characters,

If "AH12345678",

Byte 01 is 0x41 (A),

The 02nd byte is 0x48 (H),

……

The 09th byte is 0x37 (7),

The tenth byte is 0x38 (8).



	
	SN byte 02
	
	
	
	

	004
	SN byte 03
	R
	‘0’~’9’; ‘A’~’Z’
	
	

	
	SN byte 04
	
	
	
	

	005
	SN byte 05
	R
	‘0’~’9’; ‘A’~’Z’
	
	

	
	SN byte 06
	
	
	
	

	006
	SN byte 07
	R
	‘0’~’9’; ‘A’~’Z’
	
	

	
	SN byte 08
	
	
	
	

	007
	SN byte 09
	R
	‘0’~’9’; ‘A’~’Z’
	
	

	
	SN byte 10
	
	
	
	

	008
	功率等级

Rated Power
	R
	0x0000
	
	

	009
	保留字

undefined
	R
	0x0000
	
	

	010
	MCU board Version
	R
	0xFFFF
	
	Bit0-7  Grid-standard Version

Bit8-15 undefined

	011
	控制板辅助单片机软件版本号
Assistant program version
控制板启动程序版本号
bootloader software version
	R
	0XFFFF
	
	Bit0-7 启动程序 bootloader software
Bit8-15  辅助程序 Assistant program

	012
	拉弧版本号

AFCI Version
	R
	
	
	

	013
	辅助单片机版本号

Slave MCU Version
	R
	
	
	

	014
	控制板固件版本-字段2
Control panel firmware version-2
	R
	
	
	举例0x2001
高字节0x20 为三相低压储能固有

低字节0x01 为硬件版本号，出厂设定不可更改
密码for debug

	015
	控制板固件版本-主版本
Control panel firmware master version
	R
	
	
	举例：0x1001

Bit12-15：数字表示发行版本，大版本区分；F表示研发内部测试版本
Bit0-11：版本流水号

	016
	通讯板固件版本-字段1
Comm panel firmware version-1
	R
	
	
	

	017
	通讯板固件版本-字段2
Comm panel firmware version-2
	R
	
	
	

	018
	通讯板固件版本-主版本
Comm panel firmware master version
	R
	
	
	

	019
	安规类型

Safety type
	R
	
	
	

	020
	额定功率低字

Rated power low word
	R
	
	0.1W
	

	021
	额定功率高字

Rated power high word
	R
	
	0.1W
	

	022
	MPPT 路数及相数

MPPT number  and phases
	R
	[1,8]/[1,3]
	
	0x0503: five-mppts   three-phase

	023
	额定功率代码选择
	R
	[0-3]
	
	Factory only

附录一：额定功率机型选择表

	024
	电池路数
Battery input number
	R
	[0,4]
	
	0  默认值  也是1路输入

1  1路电池输入

2  2路电池输入

	025
	三相输出还是裂相输出选择
	R
	[0,1]
	
	默认值三相
0:三相输出

1:裂相输出

	026
	EU or UL

欧版或者美版选择
	
	
	
	0: EU  default value

1:UL

	027
	风扇配置
	
	
	
	Bit0  总使能

Bit1  内部风扇1

Bit2  内部风扇2

Bit3  外部风扇1

Bit4  外部风扇2

Bit5  外部风扇3

	028
	逆变器代数
	R
	[0,10]
	
	1: SG01

2:SG02

	029
	逆变器系列区分
	R
	[A,Z]
	
	26个字母顺序

参考逆变器系列区分表

	030
	InternalRTC/External RTC
	R
	
	
	InternalRTC：1
External RTC: 0

	031
	Lcd_MCU_Type
	R
	
	
	高8位：芯片类型，低8位：芯片序号

	032
	Control_MCU_Type
	R
	
	
	高8位：芯片类型，低8位：芯片序号

	033
	HV:母线电压等级

	R
	
	
	Engineer only

0:220-277VAC  IGBT=1200V

1:100-133VAC  IGBT=650V

	
	LV: TRANS_RATIO
	
	
	
	Engineer only

0：ratio=12

1：ratio=9

	034
	默认输出电压
	
	
	
	附录三：输出电压选择表

	035
	FSW for INV bridge
	
	
	
	Factory only

LV:0=15K  1=20K

	036
	Relay selfcheck
	
	
	
	Factory only

Bit0: 0-disable  1-enable

	059
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	


10可读写可变属性区，对应功能码是0x10。
	Addr
	Register meaning
	R/W
	data range
	unit
	note


	

	60
	Factory only
	R/W
	
	
	Engineer debug only

	61
	开机自检时间

self-check time
	R/W
	[0,1000]
	S
	MI

	62


	系统时间第 1 字节

system time  byte 01
	R/W
	[0,255]
	年
Year
	MI以 20 00 年为基值

Based on the year 2000

	
	系统时间第 2 字节

system time  byte 02
	R/W
	[1,12]
	月
Month
	

	63

	系统时间第 3 字节

system time  byte 03
	R/W
	[1,31]
	日

Day
	

	
	系统时间第 4 字节

system time  byte 04
	R/W
	[0,23]
	时
Hour
	

	64

	系统时间第 5 字节

system time  byte 05
	R/W
	[0,59]
	分Minute
	

	
	系统时间第 6 字节

system time  byte 06
	R/W
	[0,59]
	秒
Sec
	

	65
	
	
	
	
	

	66
	预留

Undefine
	
	
	
	

	67
	预留

Undefine
	
	
	
	

	68
	预留

Undefine
	
	
	
	

	69
	预留

Undefine
	
	
	
	

	70
	预留

Undefine
	
	
	
	

	71
	预留

Undefine
	
	
	
	

	72
	预留

Undefine
	
	
	
	

	73
	
	
	
	
	

	74
	通讯地址

Communication address
	R
	0x0000
	-
	

	75
	电压对有功响应时间

V(W)  ResponseTime
	R/W
	[0,1200]
	0.1S
	

	76
	无功响应时间

V(Q)  ResponseTime
	R/W
	[0,1200]
	0.1S
	

	77
	有功功率调节

Active-power  regulation
	R/W
	[0,1000]
	0.1%
	

	78
	无功功率调节

Reactive-power  regulation
	R/W
	[-600,600]
	0.1%
	

	79
	视在功率调节

Apparent power regulation
	R/W
	[0,1200]
	0.1%
	

	80
	开关机使能

Switch on and off enable
	R/W
	[0,1]
	-
	0：关机     1：开机MI 2：关机
0: power off 1: power on

	81
	恢复出厂使能

Factory reset enable
	R/W
	[0,1]
	
	0: disable 1: enable 3：Lockedinv

	82
	自检时间

Self-checking time
	R/W
	[0,1]
	-
	0-360 seconds

	83
	孤岛保护使能

Island protection enable
	R/W
	[0,1]
	
	0: disable 1: enable

	84
	无功使能位

	R/W
	[0,1]
	-
	需要和电压有功-V(Q)有功无功-P(Q)有功PF-P(F) 互斥

0 disable

1 PF enable

2 Q enable

	85
	GFDI使能

GFDI enable
	R/W
	[0,1]
	
	0: disable 1: enable

已使用

	86
	RCD enable
	
	
	
	0: disable 1: enable

	87
	RISO 使能
RISO enable
	R/W
	[0,1]
	
	0: disable 1: enable

	88
	R shutdown
	R/W
	[0,1]
	
	0: disable   others: enable

	89
	
	
	
	
	

	90
	
	
	
	
	

	91
	控制板EEPROM 初始使能

MCU-EEPROM initial enabled
	R/W
	[0,2]
	-
	0: 正常工作 work normal        
1: 初始化控制板 EEPROM  init mcu eeprom

	92
	通讯板EEPROM 初始使能

Comm-EEPROM initial enabled
	R/W
	
	
	0：正常 work normal

1：初始化通讯板 EEPROM init comm eeprom
3：Locekd inverter(Sunsynk)

	93
	控制板测试控制指令
Factory only
	
	
	
	Bit0   开测试使能(使能这后面的才有效)
Test enable=1 if use later bit

Bit1   开逆变器全部风扇 open all fan

Bit4   开启Gen信号继电器   open Gen singal relay

	94
	通讯板测试控制指令Factory only
	R/W
	[0,3]
	-
	Bit0   开测试使能(使能这后面的才有效)
Test enable=1 if use later bit
Bit2   闪显示板的所有LED，蜂蜜器，背光,显示红黄蓝
Flash display board for all LEDs, honey maker, backlight, display red, yellow and blue
Bit3   开启锂电池接口测试
Open lithium battery interface test
Bit5   重启液晶程序
Restart lcd

	95
	
	
	
	
	

	96
	发电量修正系数

PowerWH Factor
	R/W
	
	-0.01
	100  mean 1

111 mean 1.11

	97
	Solar输入为SPU

TEST MODE
	
	
	
	For debug only

Bit0  PV输入时电源模式

Bit1  电池输入是单向源模式


	98
	电池充电类型
Control Mode
	R/W
	-
	-
	0x0000  Lead-Battery, four-stage charging method

0x0001  Lithium battery

	99
	Equalization V
	R/W
	[3800,6100]
	0.01V
	1480 means 14.8v

	100
	Absorption V
	R/W
	[3800,6100]
	0.01V
	1440 means 14.4v

	101
	Float V
	R/W
	[3800,6100]
	0.01V
	1440 means 14.4v

	102
	电池容量
Batt Capacity
	R/W
	[0,2000]
	1 Ah
	200 means 200AH

	103
	Empty_v
	R/W
	
	0.01V
	

	104
	最小limit起作用功率
ZeroExport power
	R/W
	
	
	

	105
	均衡充几天执行一次
Equalization day cycle
	R/W
	[0 90]
	Day
	

	106
	均衡充执行时间
Equalization time
	R/W
	[0 20]
	0.5Hour
	分辨率 0.5小时
Resolution 0.5 h

[0-20]对应  0- 10小时
但是发MCU是[0-100]

	107
	温度补偿值
TEMPCO
	R/W
	[0,50]
	1mV/℃
	带有正负的int型 Signed int

	108
	电池最大充电电流
Max A Charge
	R/W
	[0,185]
	1A
	0-185A

	109
	电池最大放电电流
Max A discharge
	R/W
	[0,185]
	1A
	0-185A

	110
	Parallel Bat&Bat2
	R/W
	[0,1]
	
	For high vol three phase inverter

	111
	电池工作根据电压还是容量
battery operates according to voltage or capacity
	R/W
	
	
	根据电压 According to the voltage

根据容量 According to the capacity

2     没有电池 no battery

	112
	锂电池唤醒标志位
Li-battery wake up sign bit
	R/W
	
	
	Bit0 电池1唤醒  0=enabled  1=Disable

Bit8 电池2唤醒  0=enabled  1=Disable

	113
	电池内阻值
battery  resistance value
	R/W
	[0,6000]
	mΩ
	

	114
	电池充电效率
Battery charging efficiency
	R/W
	[0-100]
	0.1%
	983表示98.3%
983 is  98.3%

	115
	电池容量ShutDown
battery capacity ShutDown
	R/W
	[0,100]
	1%
	低容量截止点
Low capacity cutoff point

	116
	电池容量Restart
battery capacityRestart
	R/W
	[0,100]
	1%
	保护恢复点
Protection recovery point

	117
	电池容量LowBatt
battery capacityLowBatt
	R/W
	[0,100]
	1%
	

	118
	电池电压ShutDown
battery voltageShutDown
	R/W
	[3800,6100]
	0.01V
	低保护点 cutoff         41V
Low protection point cutoff 41V

	119
	电池电压Restart
battery voltageRestart
	R/W
	[3800,6100]
	0.01V
	Reboot /recover          52V

	120
	电池电压LowBatt
battery voltageLowBatt
	R/W
	[3800,6100]
	0.01V
	放电深度               46V Discharge depth 46V

	121
	发电机最大运行时间
Maximum operating time of generator
	
	
	0.1 hours
	120表示12小时
120 is 12 hours

	122
	发电机冷却时间
Generator cooling time
	
	
	0.1 hours
	120表示12小时
120 is 12 hours

	123
	发电机充电启动电压点
Generator charging Starting voltage point
	R/W
	[0000 6300]
	0.01V
	电池电压小于这个值发电机开启充电
The battery voltage is less than this value

	124
	发电机充电启动容量点
Generator charging starting capacity point
	R/W
	[0000 6300]
	1%
	电池容量小于这个值发电机开启充电
The battery capacity is less than this value

	125
	发电机对电池充电电流
Generator charges the battery  current
	R/W
	[0000 185]
	1A
	发电机对电池充电电流
The generator charges the battery

	126
	市电充电启动电压点
Grid charging Start voltage point o
	R/W
	[0000 6300]
	0.01v
	

	127
	市电充电启动容量点
Grid  charging start capacity point
	R/W
	[0000 6300]
	1%
	

	128
	市电对电池充电电流
Grid  charge  the battery  current
	R/W
	[0000 185]
	1A
	市电对电池充电电流
Grid  charge  the battery  current

	129
	发电机充电使能
Generator is charged to enable
	R/W
	
	
	

	130
	市电充电使能
Grid  is charged to enable
	R/W
	
	
	

	131
	AC couple 频率上限设置
	R/W
	5000-6500
	
	5000-6500

	132
	强制开启发电机作为负载功能
Force on generator as load function
	R/W
	
	
	前提是235号寄存器已经使能1
The premise is that register 234 has enabled 1

0 不强制 Do not force

1 强制   force

	133
	发电机输入作为负载输出使能
generator input is enabled as the load output
	R/W
	
	
	0 只作为发电机输入  only Gen use

1 智能负载输出 only smart load output

2 使能作为逆变器输入 only microinverter input 

	134
	发电机负载OFF电压
SmartLoad OFF batt Voltage
	R/W
	[3800 6300]
	0.01V
	

	135
	发电机负载OFF电量
SmartLoad OFF batt
	R/W
	[0000 100]
	1%
	

	136
	发电机负载ON电压
SmartLoad ON batt

Voltage
	R/W
	[3800 6300]
	0.01V
	

	137
	发电机负载ON电量
SmartLoad ON batt
	R/W
	[0000 100]
	1%
	

	138
	输出电压等级设定
Output voltage level setting
	R/W
	
	
	附录三：输出电压选择表

	139
	开启发电机的最小solar功率
minimum solar power required to start a generator
	R/W
	[0,8000]
	1W
	

	140
	发电机并网信号
Gen_Grid_Signal On
	
	
	
	Bit0  grid signal

Bit1  gen signal



	141
	能量管理模式
Energy management model
	
	
	
	Bit0-1  10 电池优先模式 battery first mode
       11 负载优先模式 load first mode
Bit2-3  表示被动并网功率平衡功能Represents passive grid-connected power balance function
       10 不开启 colse
       11 开启 open
Bit4-5  表示主动并网功率平衡功能 Represents active grid-connection power balance function
       10 不开启 close
       11 开启 open

	142
	limit控制功能
limit control function
	R/W
	
	0/1
	0x00 使能卖电 
sell electricity enabled

0x01 使能内置  built-in  enabled

0x02 使能外置  
extraposition  enabled



	143
	最大卖电功率

Max sell Power
	R/W
	[0,8000]
	1W
	Low Vol: 1W

High Vol:10W

	144
	外置电流传感器方向
External current sensor clamp phase

	R/W
	[xx,00]
	1W
	[11][12]

	145
	光伏卖电
Solar sell
	R/W
	
	
	0x00光伏不卖电 solar  Don't sell 0x01光伏卖电 solar sell

	146
	高级削峰填谷功能使能
Time of Use Selling  enabled
	R/W
	
	
	Bit0   0 disable  
1 enable
Bit1   Monday
 0-disable 1-enable
Bit2   Tuesday
……
Bit7   Sunday

Bit8  西班牙模式

	147
	三相ABC电网相序设定
Grid Phase
	R/W
	
	
	0  120   240

0  240   120

	148
	TOU Time1
	R/W
	[0000 2359]
	
	2359 means time 23:59

HMI range[0-287]

Communication range[0000-2355]

	149
	TOU Time2
	R/W
	[0000 2359]
	
	

	150
	TOU Time3
	R/W
	[0000 2359]
	
	

	151
	TOU Time4
	R/W
	[0000 2359]
	
	

	152
	TOU Time5
	R/W
	[0000 2359]
	
	

	153
	TOU Time6
	R/W
	[0000 2359]
	
	

	154
	TOU Time1 bat out power
	R/W
	[0000 8000]
	1W
	LV INV: 1W

HV INV:10W

	155
	TOU Time2 bat out power
	R/W
	[0000 8000]
	1W
	

	156
	TOU Time3 bat out power
	R/W
	[0000 8000]
	1W
	

	157
	TOU Time4 bat out power
	R/W
	[0000 8000]
	1W
	

	158
	TOU Time5 bat out power
	R/W
	[0000 8000]
	1W
	

	159
	TOU Time6 bat out power
	R/W
	[0000 8000]
	1W
	

	160
	TOU Time1 battery target voltage
	R/W
	[0000 6300]
	0.01V
	

	161
	TOU Time2 battery target voltage
	R/W
	[0000 6300]
	0.01V
	

	162
	TOU Time3 battery target voltage
	R/W
	[0000 6300]
	0.01V
	

	163
	TOU Time4 battery target voltage
	R/W
	[0000 6300]
	0.01V
	

	164
	TOU Time5 battery target voltage
	R/W
	[0000 6300]
	0.01V
	

	165
	TOU Time6 battery target voltage
	R/W
	[0000 6300]
	0.01V
	

	166
	1容量  1 capacity
	R/W
	[0,100]
	1%
	Soc

	167
	2容量  2 capacity
	R/W
	[0,100]
	1%
	

	168
	3容量  3 capacity
	R/W
	[0,100]
	1%
	

	169
	4容量  4 capacity
	R/W
	[0,100]
	1%
	

	170
	5容量  5 capacity
	R/W
	[0,100]
	1%
	

	171
	6容量  6 capacity
	R/W
	[0,100]
	1%
	

	172
	TOU Time1 charge enable


	R/W
	[0,1]
	
	Bit0   grid charging enable

Bit1   gen charging enable
LV inverter
Bit2   Spain GM mode
Bit3   Spain BU mode

Bit4   Spain CH mode



	173
	TOU Time2 charge enable
	R/W
	[0,1]
	
	同上

	174
	TOU Time3 charge enable
	R/W
	[0,1]
	
	同上

	175
	TOU Time4 charge enable
	R/W
	[0,1]
	
	同上

	176
	TOU Time5 charge enable
	R/W
	[0,1]
	
	同上

	177
	TOU Time6 charge enable
	R/W
	[0,1]
	
	同上

	178
	控制板特殊功能位 1
Microinverter export to grid cutoff
	R/W
	[0,1]
	
	需要全部改成两位控制 need two bits control
-00无动作-01无动作-10失能-11使能
-00Nowork-01Nowork-10Disable-11Enable
Bit0-1  10:Disable  
11:enable

Bit2-3  10:Gen peak-shaving disable
       11:Gen peak-shaving enable
Bit4- 5: 10:Grid peak-shaving disable

11:Grid peak-shaving enable

Bit6-7  10:On Grid always on disable

11:On Grid always on enable
Bit8-9  10:external relay disable

11:external relay enable
Bit10-11  10: 锂电池丢失报故障 disable
Loss of lithium battery report fault disable
11: 锂电池丢失报故障 enable
Loss of lithium battery report fault enable
Bit12-13  10: DRM使能位 disable

         11: DRM使能位 enable

Bit14-15  10:美版接地故障 disable

11:美版接地故障 enable

注意这个寄存器不能全部都使能

	179
	Force off-grid setting
	R/W
	[0,1]
	
	1：force off-grid

0:  auto

	180
	恢复并网时间
Restore connection time
	R/W
	[10 300]
	
	

	181
	Solar Arc Fault模式开启
Solar Arc Fault Mode turned on


	R/W
	[0 1]
	
	0x00 关闭 Close

0x01 开启 open

0x02 拉弧故障清零，逆变器收到02说明液晶下发清零标志了，然后自动变回01
Arc fault reset, the inverter received 02 that the LCD issued a clear mark, and then automatically back to 01

	182
	并网标准
Grid Mode
	R/W
	[0 1 ]
	
	附录一：额定功率机型选择表

	183
	电网频率设置
Grid Frequency
	R/W
	[0 1]
	
	0x00 50HZ
0x01 60hz

	184
	电网类型设置
Grid Type
现在是三相，无效
	R/W
	[0 3 ]
	
	三相系统  Three Phase

单相    Single-phase

裂相    Split-phase

	185
	电网高压保护点
Grid Vol High
	R/W
	[1800 2700]
	0.1V
	

	186
	电网低压保护点
Grid Vol Low
	R/W
	[1800 2700]
	0.1V
	

	187
	电网频率高保护点
Grid Hz High
	R/W
	[4500 6500]
	0.01Hz
	

	188
	电网频率低保护点
Grid Hz Low
	R/W
	[4500 6500]
	0.01Hz
	

	189
	发电机连接到电网输入端
The generator is connected to the grid input
	R/W
	[1 0]
	
	0   disable

1  enabled

	190
	GEN peak shaving Power
	R/W
	[0 16000]
	LV:1W

HV:10W
	

	191
	GRID peak shaving Power
	R/W
	[0 16000]
	
	

	192
	Smart Load Open Delay
	R/W
	[1 120]
	1Minute
	

	193
	输出PF值设定（有功调节）
Output PF value Settings
	R/W
	[800 1200]
	
	800表示调整到80% 1200标识调整到120%
800 for 80%, 1200 for 120%


	194
	外部继电器位
External relay bit
	R/W
	[0 0xFFFF]
	
	Bit0-8 对应8个继电器位
Bit0-8 corresponds to 8 relay bits

	195
	ARC_facTory_B高位
ARC_facTory_B high word
	R/W
	[0,65535]
	
	高位和地位组合，以数值显示即可
High and status combination, with numerical display can be

	196
	低位
Low  word
	R/W
	[0,65535]
	
	

	197
	ARC_facTory_I高位ARC_facTory_I high word
	R/W
	[0,65535]
	
	

	198
	低位
Low  word
	R/W
	[0,65535]
	
	

	199
	ARC_facTory_F高位
ARC_facTory_F high word
	R/W
	[0,65535]
	
	

	200
	低位
Low  word
	R/W
	[0,65535]
	
	

	201
	ARC_facTory_D高位
ARC_facTory_D high word
	R/W
	[0,65535]
	
	

	202
	低位
Low  word
	R/W
	[0,65535]
	
	

	203
	拉弧次数滤波
	R/W
	[0,65535]
	
	

	204
	ARC_facTory_T低位
ARC_facTory_T low word
	R/W
	[0,65535]
	
	

	205
	ARC_facTory_C高位
ARC_facTory_C high word
	R/W
	[0,65535]
	
	

	206
	低位
Low  word
	R/W
	[0,65535]
	
	

	207
	ARC_facTory_Frz高位
ARC_facTory_Frz high word
	R/W
	[0,65535]
	
	

	208
	低位
Low  word
	R/W
	[0,65535]
	
	

	209
	Ups_delay time
	R/W
	
	1S
	0   为默认
1    1S

	210
	充电电压
charging voltage
	R/W
	
	0.01V
	

	211
	放电电压
discharge voltage
	R/W
	
	0.01V
	

	212
	充电限流
charging current limiting
	R/W
	
	1A
	

	213
	放电限流
Discharge current limiting
	R/W
	
	1A
	

	214
	当前电量
Li-bat SOC
	R/W
	
	1%
	

	215
	当前电压
Li-bat voltage
	R/W
	
	0.01V
	

	216
	当前电流
Li-bat current
	R/W
	
	1A
	

	217
	当前温度
Li-bat temperature 
	R/W
	
	0.1C
	1000对应0度 1200表示20.0度 800表示 -20.0C
1000 corresponds to 0 degrees

1200 means 20.0 degrees

800 means -20.0C

	218
	离网充电限流 最大值 Maximum charge current limit
	R/W
	
	1A
	

	219
	离网放电限流 最大值
Maximum discharge current limiting
	R/W
	
	
	

	220
	锂电池告警位
Lithium battery alarm flag
	R/W
	
	
	0x0001

	221
	锂电池故障位
Lithium battery fault flag
	R/W
	[0,65535]
	
	

	222
	锂电池标志2
Lithium battery other flag
	R/W
	[0,65535]
	
	Bit0  NULL
Bit1  电池1强冲标志 Force charge

Bit2  电池2强冲标志 Force charge
Bit3  电池休眠标志 Sleep
Bit8-15 drop Voltage when float


	223
	锂电池类型
Lithium battery type
	R/W
	
	
	0x0000   中兴派能 德朗能锂
PYLON   SOLAX

通用CAN协议
0x0001  天邦达RS485modbus协议
0x0002  KOK协议
0x0003  keith

0X0004  拓派协议
0X0005  派能485协议
0X0006  杰力斯485协议
0X0007  欣旺达485协议
0X0008  欣瑞能485协议
0X0009  天邦达485协议
0X000A  晟高电气can协议


	224
	锂电池SOH
Lithium battery SOH
	
	
	
	

	225
	锂电池软件版本号
	
	
	
	

	226
	电池额定AH
	
	
	
	

	227
	锂电池硬件版本号
	R/W
	
	
	

	228
	通讯板设置功能
Comm board setting function
	R/W
	
	
	Bit0-1   时间校时 
Bit2-3   beep     
Bit4-5   AM/PM    
Bit6-7   Auto dim 
Bit14-15  Allow_Remote（11为使能，10为失能）
-00无动作 no work

-01无动作 no work

-10失能 disable

-11使能 enable

	229
	电池1厂家

Battery1 brand
	R/W
	
	
	//=====LV battery

#define HereYin 0
#define PYLON 1
#define SOLAX 2
#define DYNESS_L 3
#define CCGX 4
#define Alpha_ESS 5
#define SUNGO_CAN 6
#define VISION_CAN 7
#define WATTSONIC_CAN 8
#define KUNLAN 9
#define GSEnergy 10
#define GS_HUB 11
#define BYD_LV 12
#define AOBO 13
#define DEYE 14
#define CFE 15
#define DMEGC 16 
#define UZENERGY 17
#define GROWATT 18
//=====HV battery

#define Bat_PYLON_HV 0x01
#define Bat_DynessHV_HV 0x02
#define Bat_UZENERGY_HV 0x03
#define Bat_SOLAX_HV 0x04
#define Bat_Deye_HV 0x05
#define Bat_BYD_HV 0x06
#define Bat_JINKOBSS_HV 0x07
#define Bat_Greenway_HV 0x08
#define Bat_WTS_HV 0x09
#define Bat_FNSPOWER_HV 0x0A
#define Bat_SHOTOPOWER_HV 0x0B
#define Bat_DOWELL_HV 0x0C
#define Bat_WECO_HV 0x0D
#define Bat_ZRGP_HV 0x0E
#define Bat_CFE_HV 0x0F
#define Bat_SUNWODA_HV 0x10
#define Bat_GENIX_HV 0x11
#define Bat_THANKSUN_HV 0x12
#define Bat_TURBO_HV 0x13
#define Bat_ENOVANCE_HV 0x14
#define Bat_MLS_HV 0x15
#define Bat_LDV_HV 0x16
#define Bat_VW_HV 0x17
#define Bat_CSE_HV 0x18
#define Bat_HUAFON_HV 0x19
#define Bat_OMLIKA_HV 0x1A


	230
	电池2厂家

Battery2 brand
	
	
	
	//=====No LV battery

//=====HV battery

#define Bat_PYLON_HV 0x01
#define Bat_DynessHV_HV 0x02
#define Bat_UZENERGY_HV 0x03
#define Bat_SOLAX_HV 0x04
#define Bat_Deye_HV 0x05
#define Bat_BYD_HV 0x06
#define Bat_JINKOBSS_HV 0x07
#define Bat_Greenway_HV 0x08
#define Bat_WTS_HV 0x09
#define Bat_FNSPOWER_HV 0x0A
#define Bat_SHOTOPOWER_HV 0x0B
#define Bat_DOWELL_HV 0x0C
#define Bat_WECO_HV 0x0D
#define Bat_ZRGP_HV 0x0E
#define Bat_CFE_HV 0x0F
#define Bat_SUNWODA_HV 0x10
#define Bat_GENIX_HV 0x11
#define Bat_THANKSUN_HV 0x12
#define Bat_TURBO_HV 0x13
#define Bat_ENOVANCE_HV 0x14
#define Bat_MLS_HV 0x15
#define Bat_LDV_HV 0x16
#define Bat_VW_HV 0x17
#define Bat_CSE_HV 0x18
#define Bat_HUAFON_HV 0x19
#define Bat_OMLIKA_HV 0x1A


	231
	
	
	
	
	

	232
	CT start Selfcheck
	
	
	
	0：selfcheck end

1：start selfcheck

2：Clear check FG

	233
	Max Inport power 
	R/W
	[0,65535]
	10W
	MAX input AC power

	234
	AC Couple enable
	
	
	
	0 disable 1 enable

	235
	Track Grid-Phase
	R/W
	[0,1]
	
	0 disable  default value

1 enable

	236
	IT_SYSTEM
	R/W
	[0,1]
	
	

	237
	Active unbalance load
	R/W
	[0,1]
	
	

	238
	unbalance power trip
	R/W
	[0,65535]
	
	

	239
	测试模式下步骤设置
	R/W
	
	
	Test_State

	240
	进入厂内初测程序
	R/W
	
	
	=12345 进入

	241
	锂电池2充电电压

Li-bat2 charging voltage
	
	
	
	

	242
	锂电池2放电电压

Li-bat2 discharging voltage
	
	
	
	

	243
	充电限流
charging current limit
	
	
	
	

	244
	放电限流
Discharge current limit
	
	
	
	

	245
	当前电量
Li-bat2 SOC
	
	
	
	

	246
	当前电压
Li-bat2 voltage
	
	
	
	

	247
	当前电流
Li-bat2 current
	
	
	
	

	248
	当前温度
Li-bat2 temperature 
	
	
	
	

	249
	离网充电限流 最大值 Max charge current limit
	
	
	
	

	250
	离网放电限流 最大值
Max discharge current limit
	
	
	
	

	251
	锂电池2告警位
Li-bat2 alarm flag
	
	
	
	

	252
	锂电池2故障位
Li-bat2 fault flag
	
	
	
	

	253
	锂电池标志2
Lithium battery other flag
	R/W
	[0,65535]
	
	Bit0  NULL
Bit1  电池1强冲标志 Force charge

Bit2  电池2强冲标志 Force charge
Bit3  电池2休眠标志 Sleep


	254
	锂电池2电池类型
Lithium battery2 type
	
	
	
	

	255
	锂电池2 SOH
Lithium battery2 SOH
	
	
	
	

	256
	锂电池2软件版本号
Lithium battery2 Version
	
	
	
	

	257
	锂电池2额定AH
Lithium battery2 AH
	
	
	
	

	258
	锂电池2硬件版本号

	
	
	
	

	259
	
	
	
	
	

	260
	
	
	
	
	

	261
	
	
	
	
	

	262
	
	
	
	
	

	263
	
	
	
	
	

	264
	
	
	
	
	

	265
	
	
	
	
	

	266
	
	
	
	
	

	267
	
	
	
	
	

	268
	
	
	
	
	

	269
	Grid1_I
	
	[900,1000]
	
	Factory Only

	270
	Grid2_I
	
	
	
	Correction coefficient

	271
	Grid3_I
	
	
	
	

	272
	Grid_V_L1
	
	
	
	

	273
	Grid_V_L2
	
	
	
	

	274
	Grid_V_L3
	
	
	
	

	275
	Limit1_I
	
	
	
	

	276
	Limit2_I
	
	
	
	

	277
	Limit3_I
	
	
	
	

	278
	PV1_V
	
	
	
	

	279
	PV1_I
	
	
	
	

	280
	PV2_V
	
	
	
	

	281
	PV2_I
	
	
	
	

	282
	INV_A_I
	
	
	
	

	283
	INV_B_I
	
	
	
	

	284
	INV_C_I
	
	
	
	

	285
	INV_A_V
	
	
	
	

	286
	INV_B_V
	
	
	
	

	287
	INV_C_V
	
	
	
	

	288
	BAT1_I
	
	
	
	

	289
	BAT1_V
	
	
	
	

	290
	Gen1_I
	
	
	
	

	291
	Gen2_I
	
	
	
	

	292
	Gen3_I
	
	
	
	

	293
	Gen1_V
	
	
	
	

	294
	Gen2_V
	
	
	
	

	295
	Gen3_V
	
	
	
	

	296
	PV3_V
	
	
	
	

	297
	PV3_I
	
	
	
	

	298
	PV4_V
	
	
	
	

	299
	PV4_I
	
	
	
	

	300
	BAT2_I
	
	
	
	

	301
	BAT2_V
	
	
	
	

	302
	
	
	
	
	

	303
	
	
	
	
	

	304
	
	
	
	
	

	305
	
	
	
	
	

	306
	
	
	
	
	

	307
	
	
	
	
	

	308
	
	
	
	
	

	309
	
	
	
	
	

	310
	Solar做Wind输入使能
Solar makes Wind input enable
	R/W
	[0,1]
	
	Bit0   Solar1
Bit1   Solar2

	311
	Voltage      1
	R/W
	[500,5000]
	0.1V
	

	312
	Voltage  2
	R/W
	
	0.1V
	

	313
	Voltage  3
	R/W
	
	0.1V
	

	314
	Voltage  4
	R/W
	
	0.1V
	

	315
	Voltage  5
	R/W
	
	0.1V
	

	316
	Voltage  6
	R/W
	
	0.1V
	

	317
	Voltage  7
	R/W
	
	0.1V
	

	318
	Voltage  8
	R/W
	
	0.1V
	

	319
	Voltage  9
	R/W
	
	0.1V
	

	320
	Voltage  10
	R/W
	
	0.1V
	

	321
	Voltage  11
	R/W
	
	0.1V
	

	322
	Voltage  12
	R/W
	
	0.1V
	

	323
	Current   1
	R/W
	[0-200]
	0.1A
	

	324
	Current 2
	R/W
	
	0.1A
	

	325
	Current 3
	R/W
	
	0.1A
	

	326
	Current 4
	R/W
	
	0.1A
	

	327
	Current 5
	R/W
	
	0.1A
	

	328
	Current 6
	R/W
	
	0.1A
	

	329
	Current 7
	R/W
	
	0.1A
	

	330
	Current 8
	R/W
	
	0.1A
	

	331
	Current 9
	R/W
	
	0.1A
	

	332
	Current 10
	R/W
	
	0.1A
	

	333
	Current 11
	R/W
	
	0.1A
	

	334
	Current 12
	R/W
	
	0.1A
	

	335
	离网平衡 Stop SOC
	
	
	
	For parallel system

	336
	并联1
Parallel-1
	
	
	
	Bit0           1:Parallel Enable 
0: Parallel Disable
Bit1           1:Master   0:Slave
Bit2-7        Void
Bit8-9   Phase(00:A,01:B,10:C,11:void)
Bit10-15    Modbus SN(0-63)

	337
	并联2
Parallel-2
	
	
	
	

	338
	预留

Undefine
	
	
	
	

	339
	预留

Undefine
	
	
	
	

	340
	光伏最大卖电功率
Max Solar Sell Power
	
	R/W
	1W
	Low Vol:1W

High Vol:10W

	341
	Special_Function3


	
	
	
	For debug.   engineer only

Bit0  Bat1&2 voltage calibration from BMS

Bit1  MinPF enable

Bit2

	342
	Italy selfcheck mode
	R/W
	
	
	0:Disable

1:Enable

	343
	Italy  loacal  mode
	R/W
	
	
	0:wide range

1: narrowrange

	344
	电网信息监测方式

Grid check from Meter or CT
	R/W
	
	     
	BIT00:
0：CT

1：Meter   
BIT01: -BIT15: undefine

	345
	电表厂家信息
	
	
	
	0：预留

1：Eastron 东鸿

2：CHNT   正泰

	346
	Meter limit mode
	
	
	[0,1]
	0: AVE
1: MIN

	347
	外置CT变比

CT ratio
	R/W
	
	30<-->
30:1
	U16

	348
	
	
	
	
	

	349
	
	
	
	
	

	350
	电压重连上限

(Reconn.Vol_Max)
	R/W
	[0,10000]
	0.1v
	1000:100.0v

2300:230.0v

	351
	电压重连下限

(Reconn.Vol_Min)
	R/W
	[0,10000]
	0.1v
	1000:100.0v

2300:230.0v

	352
	频率重连上限

(Reconn.Freq_Max)
	R/W
	[0,10000]
	0.01Hz
	5000:50Hz
6000:60Hz

	353
	频率重连下限

(Reconn.Freq_Min)
	R/W
	[0,10000]
	0.01Hz
	5000:50Hz

6000:60Hz

	354
	过压1

(Over_Vol.Trip1_Value)
	R/W
	[0,10000]
	0.1v
	1000:100.0v

2300:230.0v

	355
	过压2

(Over_Vol.Trip2_Value)
	R/W
	[0,10000]
	0.1v
	1000:100.0v

2300:230.0v

	356
	欠压1

(Under_Vol.Trip1_Value)
	R/W
	[0,10000]
	0.1v
	1000:100.0v

2300:230.0v

	357
	欠压2

(Under_Vol.Trip2_Value)
	R/W
	[0,10000]
	0.1v
	1000:100.0v

2300:230.0v

	358
	过频1

(Over_Freq.Trip1_Value)
	R/W
	[0,10000]
	0.01Hz
	5000:50Hz
6000:60Hz

	359
	过频2

(Over_Freq.Trip2_Value)
	R/W
	[0,10000]
	0.01Hz
	5000:50Hz
6000:60Hz

	360
	欠频1

(Under_Freq.Trip1_Value)
	R/W
	[0,10000]
	0.01Hz
	5000:50Hz
6000:60Hz

	361
	欠频2

(Under_Freq.Trip2_Value)
	R/W
	[0,10000]
	0.01Hz
	5000:50Hz
6000:60Hz

	362
	长时间过压

(Over_Vol_Long.Trip1_Value)
	R/W
	[0,10000]
	0.1v
	1000:100.0v

2300:230.0v

	363
	电压-无功 Lock in

Volt_VAR
	R/W
	[0,10000]
	0.01%Pn
	 10000:100%Pn

	364
	电压-无功 Lock out

Volt_VAR
	R/W
	[0,10000]
	0.01%Pn
	

	365
	电压-有功模式使能

(V_Watt.Ena)
	R/W
	[0,1]
	NO
	0:disable

1:enabled

	366
	电压-有功模式，

电压点1

(V_Watt.V1)
	R/W
	[0,10000]
	0.01%
	0:0%额定电压

5000:50%额定电压

10000:100%额定电压

（电压点1小于等于电压点2）

	367
	电压-有功模式，

有功点1

(V_Watt.W1)
	R/W
	[0,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定功率

	368
	电压-有功模式，

电压点2

(V_Watt.V2)
	R/W
	[0,10000]
	0.01%
	0:0%额定电压

5000:50%额定电压

10000:100%额定电压

（电压点2小于等于电压点3）

	369
	电压-有功模式，

有功点2

(V_Watt.W2)
	R/W
	[0,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定功率

	370
	电压-有功模式，

电压点3
(V_Watt.V3)
	R/W
	[0,10000]
	0.01%
	0:0%额定电压

5000:50%额定电压

10000:100%额定电压

（电压点3小于等于电压点4）

	371
	电压-有功模式，

有功点3
(V_Watt.W3)
	R/W
	[0,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定功率

	372
	电压-有功模式，

电压点4
(V_Watt.V4)
	R/W
	[0,10000]
	0.01%
	0:0%额定电压

5000:50%额定电压

10000:100%额定电压

（电压点4最大）

	373
	电压-有功模式，

有功点4
(V_Watt.W4)
	R/W
	[0,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定功率

	374
	电压-无功模式使能

(Volt_VAR.Ena)
	R/W
	[0,1]
	None
	Bit0:  0:disable   1:enabled

Bit1:  0:Pref=Pn  1:Pref=Pmax

	375
	电压-无功模式，

电压点1

(Volt_VAR.V1)
	R/W
	[0,10000]
	0.01%
	0:0%额定电压

5000:50%额定电压

10000:100%额定电压

（电压点1小于等于电压点2）

	376
	电压-无功模式，

无功点1

(Volt_VAR.VAr1)
	R/W
	[-7000,7000]
	0.01%
	0:0%额定功率

-7000:-70%额定功率

7000:70%额定功率

	377
	电压-无功模式，

电压点2

(Volt_VAR.V2)
	R/W
	[0,10000]
	0.01%
	0:0%额定电压

5000:50%额定电压

10000:100%额定电压

（电压点2小于等于电压点3）

	378
	电压-无功模式，

无功点2

(Volt_VAR.VAr2)
	R/W
	[-7000,7000]
	0.01%
	0:0%额定功率

-7000:-70%额定功率

7000:70%额定功率

	379
	电压-无功模式，

电压点3
(Volt_VAR.V3)
	R/W
	[0,10000]
	0.01%
	0:0%额定电压

5000:50%额定电压

10000:100%额定电压

（电压点3小于等于电压点4）

	380
	电压-无功模式，

无功点3

(Volt_VAR.VAr3)
	R/W
	[-7000,7000]
	0.01%
	0:0%额定功率

-7000:-70%额定功率

7000:70%额定功率

	381
	电压-无功模式，

电压点4

(Volt_VAR.V4)
	R/W
	[0,10000]
	0.01%
	0:0%额定电压

5000:50%额定电压

10000:100%额定电压

（电压点4最大）

	382
	电压-无功模式，

无功点4

(Volt_VAR.VAr4)
	R/W
	[-7000,7000]
	0.01%
	0:0%额定功率

-7000:-70%额定功率

7000:70%额定功率

	383
	频率-有功参数模式使能

(Freq_Watt_P.Ena)
	R/W
	[0,7]
	NO
	Bit0: enabled（欠频加载使能）

Bit1: enabled（过频降载使能）

Bit2：过频冻结禁止

Bit3：欠频冻结禁止

Bit4：Pref_enable


	384
	频率-有功参数模式，

欠频退出频率
(Freq_Watt_P.Under_StopHz

)
	R/W
	[0,200]
	0.1%
	200:20%下垂率：50Hz*20%=10Hz

	385
	频率-有功参数模式，

欠频_频率点1
(F_Watt_P.Under_Hz1)
	R/W
	[0,200]
	0.1%
	200:20%下垂率：50Hz*20%=10Hz

	386
	频率-有功参数模式，

欠频下垂率1
(F_Watt_P.Under_WGra1)
	R/W
	[0,10000]
	0.001Hz
	10000:10Hz

	387
	频率-有功参数模式，

欠频_频率点1的

启动延时
	R/W
	[0-65535]
	0.1S
	

	388
	频率-有功参数模式，

欠频退出频率的

停止延时
	R/W
	[0-65535]
	0.1S
	

	389
	频率-有功参数模式，

过频退出频率点(F_Watt_P.Over_StopHz)
	R/W
	[4500,6500]
	0.01Hz
	4500:45.00Hz

5000:50.00Hz

6500:65.00Hz

	390
	频率-有功参数模式，

过频频率点1
(F_Watt_C.Over_Hz1)
	R/W
	[0,30000]
	%Prated/min
	100:10.0%Prated/min

1000:100.0%Prated/min

30000:3000.0%Prated/min

	391
	频率-有功参数模式，

过频下垂率1
(F_Watt_C.Over.WGra1)
	
	
	
	

	392
	频率-有功参数模式，

过频_频率点1的

启动延时
	R/W
	[0-65535]
	0.1S
	

	393
	频率-有功参数模式，

过频退出频率的

停止延时
	R/W
	[0-65535]
	0.1S
	

	394
	预留
	
	
	
	

	395
	有功-无功模式使能

(Watt_VAr.Ena)
	R/W
	[0,1]
	NO
	0:disable

1:enabled

	396
	有功-无功模式，

有功点1

(Watt_VAr.W1)
	R/W
	[-10000,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定功率

（有功点1小于等于有功点2）

	397
	有功-无功模式，

无功点1

(Watt_VAr.VAr1)
	R/W
	[-7000,7000]
	0.01%
	0:0%额定功率

-7000:-70%额定功率

7000:70%额定功率

	398
	有功-无功模式，

有功点2

(Watt_VAr.W2)
	R/W
	[-10000,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定功率

（有功点2小于等于有功点3）

	399
	有功-无功模式，

无功点2

(Watt_VAr.VAr2)
	R/W
	[-7000,7000]
	0.01%
	0:0%额定功率

-7000:-70%额定功率

7000:70%额定功率

	400
	有功-无功模式，

有功点3
(Watt_VAr.W3)
	R/W
	[-10000,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定功率

（有功点3小于等于有功点4）

	401
	有功-无功模式，

无功点3

(Watt_VAr.VAr3)
	R/W
	[-7000,7000]
	0.01%
	0:0%额定功率

-7000:-70%额定功率

7000:70%额定功率

	402
	有功-无功模式，

有功点4

(Watt_VAr.W4)
	R/W
	[-10000,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定电压

（有功点4最大）

	403
	有功-无功模式，

无功点4

(Watt_VAr.VAr4)
	R/W
	[-7000,7000]
	0.01%
	0:0%额定功率

-7000:-70%额定功率

7000:70%额定功率

	404
	有功-功率因素模式使能

(Watt_PF.Ena)
	R/W
	[0,1]
	NO
	0:disable

1:enabled

	405
	有功-功率因素模式，

有功点1

(Watt_PF.W1)
	R/W
	[-10000,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定功率

（有功点1小于等于有功点2）

	406
	有功-功率因素模式，

功率因素点1

(Watt_PF.PF1)
	R/W
	[8000,10000],

[-8000,-10000]

	0.0001
	10000:功率因素为1

8000:功率因素为0.8

-8000:功率因素为-0.8
-10000:功率因素为-1

	407
	有功-功率因素模式，

有功点2

(Watt_PF.W2)
	R/W
	[-10000,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定功率

（有功点2小于等于有功点3）

	408
	有功-功率因素模式，

功率因素点2

(Watt_PF.PF2)
	R/W
	[8000,10000],

[-8000,-10000]

	0.0001
	10000:功率因素为1

8000:功率因素为0.8

-8000:功率因素为-0.8
-10000:功率因素为-1

	409
	有功-功率因素模式，

有功点3
(Watt_PF.W3)
	R/W
	[-10000,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定功率

（有功点3小于等于有功点4）

	410
	有功-功率因素模式，

功率因素点3

(Watt_PF.PF3)
	R/W
	[8000,10000],

[-8000,-10000]

	0.0001
	10000:功率因素为1

8000:功率因素为0.8

-8000:功率因素为-0.8
-10000:功率因素为-1

	411
	有功-功率因素模式，

有功点4

(Watt_PF.W4)
	R/W
	[-10000,10000]
	0.01%
	0:0%额定功率

5000:50%额定功率

10000:100%额定电压

（有功点4最大）

	412
	有功-功率因素模式，

功率因素点4

(Watt_PF.PF4)
	R/W
	[8000,10000],

[-8000,-10000]

	0.0001
	10000:功率因素为1

8000:功率因素为0.8

-8000:功率因素为-0.8
-10000:功率因素为-1

	413
	CA_Vstart
	
	
	
	

	414
	CA_Vstop
	
	
	
	

	415
	正常上升斜率
Normal upward slope
	R/W
	[1 100]
	1%
	

	416
	软启动上升速率
Soft start rise rate
	R/W
	[1 100]
	1%
	

	417
	过压1触发延时

(Over_Vol.Trip1_delay)
	R/W
	[1,6000]

0.1S-600S
	0.1S
	

	418
	过压2

(Over_Vol.Trip2_ delay)
	R/W
	[1, 6000]
	0.1S
	

	419
	欠压1

(Under_Vol.Trip1_ delay)
	
	[1,6000]
	0.1S
	

	420
	欠压2

(Under_Vol.Trip2_ delay)
	
	[1, 6000]
	0.1S
	

	421
	过频1

(Over_Freq.Trip1_ delay)
	
	[1,6000]
	0.1S
	

	422
	过频2

(Over_Freq.Trip2_ delay)
	
	[1, 6000]
	0.1S
	

	423
	欠频1

(Under_Freq.Trip1_ delay)
	
	[1,6000]
	0.1S
	

	424
	欠频2

(Under_Freq.Trip2_ delay)
	
	[1, 6000]
	0.1S
	

	425
	
	
	
	
	

	426
	
	
	
	
	

	427
	
	
	
	
	

	428
	
	
	
	
	

	429
	
	
	
	
	

	430
	
	
	
	
	For debug

	……
	
	
	
	
	

	480
	有功-功率因数 Lock in

Watt_PF
	R/W
	[0,10000]
	0.01%Pn
	 10000:100%Pn

	481
	有功-功率因数 Lock out

Watt_PF
	R/W
	[0,10000]
	0.01%Pn
	

	482
	高低穿使能

L_HVRT_EN
	R/W
	
	
	Bit0:LVRT enable

Bit1:HVRT enable

Bit8:ZeroCurrent disable

	483
	LVRT1
	R/W
	[0,10000]
	0.01%
	

	484
	LVRT2
	R/W
	[0,10000]
	0.01%
	

	485
	HVRT1
	R/W
	[0,10000]
	0.01%
	

	486
	HVRT2
	R/W
	[0,10000]
	0.01%
	

	487
	HVRT3
	R/W
	[0,10000]
	0.01%
	

	488
	LVRT1_time
	R/W
	[0,32768]
	 10ms
	

	489
	LVRT2_time
	R/W
	[0,32768]
	 10ms
	

	490
	HVRT1_time
	R/W
	[0,32768]
	 10ms
	

	491
	HVRT2_time
	R/W
	[0,32768]
	 10ms
	

	492
	HVRT3_time
	R/W
	[0,32768]
	 10ms
	

	493
	L_HVRT_status
	R/W
	[0,1]
	
	0:零电池

1：保持进入之前的电流

	……
	
	
	
	
	

	499
	
	
	
	
	

	
	
	
	
	
	


03只读实时属性区，对应功能码是0x03。
	Addr
	Register meaning
	R/W
	data range
	unit
	note


	

	500
	运行状态

run  state
	R
	[0,5]
	-
	0000  待机 standby

0001  自检 selfcheck

0002  正常 normal

0003  告警 alarm

0004  故障 fault
0005  激活中

	501
	逆变器电网侧当日有功发电量

active power generation of today
	R
	[-32768,32767]
	0.1kWh
	

	502
	逆变器电网侧当日无功发电量

reactive power generation of today
	R
	[-32768,32767]
	0.1kVarh
	

	503
	当日并网时间

Grid connection time of today
	R
	[0,65535]
	S
	

	504
	逆变器电网侧总有功发电量低字

active power generation of total low byte
	R
	[0,0xFFFFFFFF]
	0.1kWh
	

	505
	逆变器电网侧总有功发电量高字

active power generation of total high byte
	R
	
	
	

	506
	逆变器电网侧总无功发电量低字

reactive power generation of total low byte
	
	
	
	

	507
	逆变器电网侧总无功发电量高字

reactive power generation of total high byte
	
	
	
	

	508
	逆变器状态位1
	R
	
	
	Debug only 调试用，无意义

Bit0:内部风扇存在位；1有  0无

Bit1:外部风扇存在位；1有  0无

	509
	逆变器状态位1
	R
	
	
	Debug only 调试用，无意义

	510
	发电量数据-预留
	R
	
	
	

	511
	发电量数据-预留
	R
	
	
	

	512
	发电机历史工作时间低字节
	R
	
	0.1h
	

	513
	发电机历史工作时间高字节
	R
	
	0.1h
	

	514
	电池当日充电量

Today charge of the battery
	R
	
	0.1kwh
	

	515
	电池当日放电量

Today discharge of the battery
	R
	
	0.1kwh
	

	516
	电池累计充电量低字

Total charge of the battery low byte
	R
	
	0.1kwh
	

	517
	电池累计充电量高字

Total charge of the battery high byte
	R
	
	0.1kwh
	

	518
	电池累计放电量低字

Total discharge of the battery low byte
	R
	
	0.1kwh
	

	519
	电池累计放电量高字

Total discharge of the battery high byte
	R
	
	0.1kwh
	

	520
	电网当日购电量

Day_GridBuy_Power Wh
	R
	
	0.1kwh
	

	521
	电网当日卖电量

Day_GridSell_Power Wh
	R
	
	0.1kwh
	

	522
	电网累计购电量低字

Total_GridBuy_Power Wh_low word
	R
	
	0.1kwh
	

	523
	电网累计购电量高字

Total_GridBuy_Power Wh_high word
	R
	
	0.1kwh
	

	524
	电网累计卖电量低字

Total_GridSell_Power Wh_low word
	R
	
	0.1kwh
	

	525
	电网累计卖电量高字

Total_GridSell_Power Wh_high word
	R
	
	0.1kwh
	

	526
	当日用电量

Day_Load_Power Wh
	R
	
	0.1kwh
	

	527
	累计用电量低字

Total_Load_Power Wh_low word
	R
	
	0.1kwh
	

	528
	累计用电量高字

Total_Load_Power Wh_high word
	R
	
	0.1kwh
	

	529
	当日总PV发电量

Day_PV_Power Wh
	R
	[0,65535]
	0.1kWh
	

	530
	当日PV-1发电量

Day_PV-1_Power Wh
	R
	
	0.1kWh
	预留

	531
	当日PV-2发电量

Day_PV-2_Power Wh
	R
	
	0.1kWh
	预留

	532
	当日PV-3发电量

Day_PV-3_Power Wh
	R
	
	0.1kWh
	预留

	533
	当日PV-4发电量

Day_PV-4_Power Wh
	R
	
	0.1kWh
	预留

	534
	历史PV发电量低字

Total PV_power Wh_low word
	R
	
	0.1kWh
	预留

	535
	历史PV发电量高字

Total PV_power Wh_high word
	R
	
	0.1kWh
	

	536
	发电机日发电量
	R
	
	0.1kWh
	

	537
	发电机总发电量低字节
	R
	
	0.1kWh
	

	538
	发电机总发电量高字节
	R
	
	0.1kWh
	

	539
	发电机日工作时间
Generator working hours per day
	R
	
	0.1h
	

	540
	 DC变压器温度
(DCTransformer temperature)
	R
	[0,3000]
	0.1℃
	偏移1000

	541
	散热片温度

Heat sink temperature
	R
	[0,3000]
	0.1℃
	

	542
	预留温度1
undefine
	R
	[0,3000]
	0.1℃
	

	543
	预留温度2
undefine
	R
	[0,3000]
	0.1℃
	

	544
	DRMs_Data
	R
	[0,3000]
	0.1℃
	bit0-bit8依次表示DRM0-DRM8

	545
	负载年用电量低字节
Yer_Loadwh_L
	R
	[0,0xFFFF]
	0.1KWH
	

	546
	负载年用电量高字节
Yer_Loadwh_H
	R
	[0,0xFFFF]
	0.1KWH
	

	547
	测试模式下步骤Test_State
	
	
	
	

	548
	通讯板的故障状态
Failure status of communication board
	R
	[0,0xFFFF]
	
	Bit0   Flash chip error
Bit1   time error
Bit2   EEPROM error

	549
	MCU测试标志位
MCU test flag
	R
	
	
	Bit0   拉弧通讯标志 Arc pull communication sign

Bit1   可并联CAN通讯 Parallel CAN communication
Bit2   OutSide Fan_FG

Bit3   InSide  Fan_FG

Bit4   Meter FG

Bit5   拉弧触发标识

Bit6   拉弧磁环1自检

……

Bit13  拉弧磁环8自检

ATE拉弧自检测试使用Bit说明
低压三相（1磁环）：

Bit6   拉弧磁环1自检
高压（2磁环）：

Bit8   拉弧磁环1自检

Bit9   拉弧磁环2自检


	550
	LCD测试标志位
LCD test flag
	R
	0x0000
	
	Bit8   锂电接口RS485 Lithium electric interface RS485

Bit9   锂电接口CAN Lithium electric interface CAN

Bit10  按键1234 key1234

Bit11  液晶中断状态 lcd interrupt status

	551
	开关机状态
Turn off/on status
	R
	
	
	低4位表示开关信号
0000 关机   power off

0001 开机    power on

	552
	AC侧继电器状态
AC realy status
	R
	
	
	off

on

Bit0     INV继电器 INV relay

Bit1     负载继电器  预留 undefine
Bit2     电网继电器 grid relay

Bit3     发电机继电器 gen relay
Bit4     电网供电继电器 grid give power to relay
Bit7     干接点 Dry contact1
Bit8     干接点 Dry contact2()


	553
	告警信息第 1 字

Warning message word 1
	R
	[0,65535]
	
	Bit0: reserved
Bit1:风扇故障   FAN_WARN

Bit2:电网相位错误  grid phase wrong

Bit3:

……

Bit15

	554
	告警信息第 2 字

Warning message word 2
	R
	[0,65535]
	
	Bit0

Bit1

……

Bit14 锂电池丢失告警
Bit15 并联通讯质量告警

	555
	故障信息第 1字

Fault information word 1
	R
	[0,65535]
	
	见故障信息编码表

	556
	故障信息第 2字

Fault information word 2
	R
	[0,65535]
	
	

	557
	故障信息第 3 字

Fault information word 3
	R
	[0,65535]
	
	

	558
	故障信息第 4 字

Fault information word 4
	R
	[0,65535]
	
	

	559
	WorkFlag.ON_OFF_Trip_DATA
	R
	
	
	

	560
	调试数据Debug Data
	R
	
	
	Factory test only

	……
	……共24个寄存器
	
	
	
	

	583
	调试数据Debug Data
	R
	0
	
	

	584
	
	
	
	
	

	585
	预留的电池温度传感器值
	R
	
	
	

	586
	电池1温度
Battery1 temperature
	R
	[0,3000]
	0.1℃
	

	587
	电池1电压
Battery-1 voltage
	R
	
	L：0.01V

H：0.1V
	

	588
	电池1的电量
Battery-1 SOC
	R
	[0,100]
	1%
	

	589
	电池2的电量
Battery-2 SOC
	R
	[0,100]
	1%
	

	590
	电池输出功率
Battery output  power
	R
	
	H:1W

H:10W
	S16

	591
	电池1电流
Battery1 Current
	R
	
	0.01A
	S16

	592
	电池校正后的容量Corrected_AH
	R
	[0,3000]
	1AH
	100 is 100AH

	593
	电池2电压
Battery-2 voltage
	R
	
	L：0.01V

H：0.1V
	

	594
	电池2电流
Battery2 Current
	R
	
	
	

	595
	电池2功率
Battery2 Power
	R
	
	L:1W

H:10W
	

	596
	电池2温度
Battery2 temperature
	R
	
	
	

	597
	CT自检结果
	R
	
	
	Bit0  CTA   1 SUCC  0 FAIL

Bit1  CTB

Bit2  CTC

	598
	电网侧相电压A
Grid phase voltage A
	R
	
	0.1V
	

	599
	电网侧相电压B
Grid phase voltage B
	R
	
	0.1V
	

	600
	电网侧相电压C
Grid phase voltage C
	R
	
	0.1V
	

	601
	电池1的负电流

	R
	
	0.1V
	

	602
	电池2的负电流

	R
	
	0.1V
	

	603
	电网侧线电压CA
Grid line voltage CA
	R
	
	0.1V
	

	604
	电网侧内侧A相功率低16位
A phase power on the inner side of the grid
	R
	
	1W
	S16

	605
	电网侧内侧B相功率低16位
B phase power on the inner side of the grid
	R
	
	1W
	S16

	606
	电网侧内侧C相功率低16位
C phase power on the inner side of the grid
	R
	
	1W
	S16

	607
	电网侧-内侧总有功功率低16位 
Total active power from side to side of the grid
	R
	
	1W
	S16

	608
	电网侧-内侧总视在功率低16位 
Grid side - inside total apparent power
	R
	
	1W
	预留

	609
	电网侧频率
Grid-side frequency
	R
	
	
	

	610
	电网侧内侧电流A
grid side inner current A
	R
	
	0.01A
	S16

	611
	电网侧内侧电流B
grid side inner current B
	R
	
	0.01A
	S16

	612
	电网侧内侧电流C
grid side inner current C
	R
	
	0.01A
	S16

	613
	电网外置-电流A
Out-of-grid - current A
	R
	
	0.01A
	S16

	614
	电网外置-电流B
Out-of-grid - current B
	R
	
	0.01A
	S16

	615
	电网外置-电流C
Out-of-grid - current C
	R
	
	0.01A
	S16

	616
	电网外置-功率A低16位 

Out-of-grid -power A
	R
	
	1W
	S16

	617
	电网外置-功率B低16位
Out-of-grid -power B
	R
	
	1W
	S16

	618
	电网外置-功率C低16位
Out-of-grid -power C高16位
	R
	
	1W
	S16

	619
	电网外置-总有功功率低16位
Out-of-grid –total power 
	R
	
	1W
	S16

	620
	电网外置-总视在功率低16位Out-of-grid –total apparent power
	R
	
	1VA
	S16

	621
	并网功率因数 PF
Grid-connected power factor PF
	R
	R/W
	[0,1000]
	真实值*1000

	622
	电网侧A相功率低16位
Grid side A-phase power

Low_Word
	R
	
	1W
	以下三个寄存器根据内置外置设置变化
The following three registers vary according to the built-in and external Settings

	623
	电网侧B相功率低16位
Grid side B-phase power

Low_Word
	R
	
	1W
	

	624
	电网侧C相功率低16位
Grid side C-phase power

Low_Word
	R
	
	1W
	

	625
	电网侧-总有功功率低16位
Grid side total power 
Low_Word
	R
	
	1W
	

	626
	
	
	
	
	

	627
	逆变器输出相电压A
Inverter output phase voltage A
	R
	
	0.1V
	

	628
	逆变器输出相电压B

Inverter output phase voltage B
	R
	
	0.1V
	

	629
	逆变器输出相电压C

Inverter output phase voltage C
	R
	
	0.1V
	

	630
	逆变器输出相电流A
Inverter output phase current A
	R
	
	0.01A
	S16

	631
	逆变器输出相电流B
Inverter output phase 

current B
	R
	
	0.01A
	S16

	632
	逆变器输出相电流C
Inverter output phase current C
	R
	
	0.01A
	S16

	633
	逆变器输出相功率A低16位
Inverter output phase 

power A Low_Word
	R
	
	1W
	S16

	634
	逆变器输出相功率B
Inverter output phase低16位 

power B Low_Word
	R
	
	1W
	S16

	635
	逆变器输出相功率C低16位
Inverter output phase 

power C Low_Word
	
	
	1W
	S16

	636
	逆变器输出总有功功率低16位
Inverter output total 

power Low_Word
	R
	
	1W
	S16

	637
	逆变器输出总视在功率低16位

Inverter output total apparent power Low_Word
	R
	
	1W
	S16

	638
	逆变器频率
Inverter frequency
	R
	
	0.01Hz
	U16

	639
	
	R
	
	
	

	640
	UPS负载侧相功率A低16位
UPS load-side phase power A Low_Word
	R
	
	1W
	U16

	641
	UPS负载侧相功率B低16位
UPS load-side phase power B

Low_Word
	R
	
	1W
	U16

	642
	UPS负载侧相功率C低16位
UPS load-side phase power C

Low_Word
	R
	
	1W
	U16

	643
	UPS负载侧总功率低16位
UPS load-sidetotal power

Low_Word
	R
	
	1W
	U16

	644
	负载测相电压A
Load phase voltage A
	R
	
	0.1V
	U16

	645
	负载测相电压B
Load phase voltage B
	R
	
	0.1V
	U16

	646
	负载测相电压C
Load phase voltage C
	
	
	0.1V
	U16

	647
	负载测电流A  无效
Load phase current A no use
	R
	
	0.01A
	S16

	648
	负载测电流B  无效
Load phase current B no use
	R
	
	0.01A
	S16

	649
	负载测电流C  无效
Load phase current C no use
	R
	
	0.01A
	S16

	650
	负载侧相功率A低16位
Load phase power A_L_Word
	R
	
	1W
	S16

	651
	负载侧相功率B低16位
Load phasepowerB

Low_Word
	R
	
	1W
	S16

	652
	负载侧相功率C低16位
Load phase poweC

Low_Word
	R
	
	1W
	S16

	653
	负载侧总有功功率低16位
Load totalpower

Low_Word
	R
	
	1W
	S16

	654
	负载侧总视在功率  预留
Load phase apparent power undefine  Low_Word
	R
	
	1W
	S16

	655
	负载频率
Load frequency
	R
	
	0.01Hz
	

	656
	负载侧相功率A高16位
Load phase power A

High_Word
	R
	
	1W
	S16

	657
	负载侧相功率B高16位
Load phase power B

High_Word
	R
	
	1W
	S16

	658
	负载侧相功率C高16位    
Load phase power C

High_Word
	R
	
	1W
	S16

	659
	负载侧总有功功率高16位
Load totalpower

High_Word
	R
	
	1W
	S16

	660
	负载侧总视在功率高16位   

预留
Load phase apparent power undefine

High_Word
	R
	
	1W
	S16

	661
	Gen端口的相电压A
Phase voltage of Gen port A
	R
	
	0.1V
	

	662
	Gen端口的相电压B
Phase voltage of Gen port B
	R
	
	0.1V
	

	663
	Gen端口的相电压C

Phase voltage of Gen port C
	R
	
	0.1V
	

	664
	Gen端口的功率A低16位
Phase power of Gen port A

Low_Word
	R
	
	1W
	

	665
	Gen端口的功率B低16位
Phase power of Gen port B

Low_Word
	R
	
	1W
	

	666
	Gen端口的功率C低16位
Phase power of Gen port C

Low_Word
	R
	
	1W
	

	667
	Gen端口的总功率低16位  
total power of Gen port

Low_Word
	R
	
	1W
	

	668
	Gen端口的功率A高16位
Phase power of Gen port A

High_Word
	R
	
	1W
	

	669
	Gen端口的功率B高16位
Phase power of Gen port B

High_Word
	R
	
	1W
	

	670
	Gen端口的功率C高16位
Phase power of Gen port C

High_Word
	R
	
	1W
	

	671
	Gen端口的总功率高16位
total power of Gen port

High_Word
	R
	
	1W
	

	672
	PV1输入功率
PV1 input power
	R
	
	L:1W

H:10W
	

	673
	PV2输入功率
PV2 input power
	R
	
	L:1W

H:10W
	

	674
	PV3输入功率
PV3 input power
	R
	
	L:1W

H:10W
	

	675
	PV4输入功率
PV4 input power
	R
	
	L:1W

H:10W
	

	676
	直流电压1

Dc voltage 1
	R
	[0,65535]
	0.1V
	

	677
	直流电流1
Dc current 1
	R
	[0,65535]
	0.1A
	

	678
	直流电压2

Dc voltage 2
	R
	[0,65535]
	0.1V
	

	679
	直流电流2

Dc current 2
	R
	[0,65535]
	0.1A
	

	680
	直流电压3

Dc voltage 3
	R
	[0,65535]
	0.1V
	

	681
	直流电流3

Dc current 3
	R
	[0,65535]
	0.1A
	

	682
	直流电压4

Dc voltage 4
	R
	[0,65535]
	0.1V
	

	683
	直流电流4

Dc current 4
	R
	[0,65535]
	0.1A
	

	684
	预留
	R
	
	
	

	685
	预留
	R
	
	
	

	686
	预留
	R
	
	
	

	687
	电网侧A相功率高16位
Grid side A-phase power

high _Word
	R
	
	1W
	以下三个寄存器根据内置外置设置变化
The following three registers vary according to the built-in and external Settings

	688
	电网侧B相功率高16位
Grid side B-phase power

high _Word
	R
	
	1W
	

	689
	电网侧C相功率高16位
Grid side C-phase power

high _Word
	R
	
	1W
	

	690
	电网侧-总有功功率高16位
Grid side total power 
high_Word
	R
	
	1W
	

	691
	逆变器输出相功率A高16位
Inverter output phase 

power A high_Word
	R
	
	1W
	S16

	692
	逆变器输出相功率B高16位
Inverter output phase power B Low_Word
	R
	
	1W
	S16

	693
	逆变器输出相功率C高16位
Inverter output phase 

power C high _Word
	
	
	1W
	S16

	694
	逆变器输出总有功功率高16位
Inverter output total 

power high _Word
	R
	
	1W
	S16

	695
	逆变器输出总视在功率高16位
Inverter output total apparent power high _Word
	R
	
	1W
	S16

	696
	UPS负载侧相功率A高16位
UPS load-side phase power A high _Word
	R
	
	1W
	U16

	697
	UPS负载侧相功率B高16位
UPS load-side phase power B high _Word
	R
	
	1W
	U16

	698
	UPS负载侧相功率C高16位
UPS load-side phase power C high _Word
	R
	
	1W
	U16

	699
	UPS负载侧总功率高16位
UPS load-sidetotal power

high _Word
	R
	
	1W
	U16

	700
	电网侧内侧A相功率高16位
A phase power on the inner side of the grid high _Word
	R
	
	1W
	S16

	701
	电网侧内侧B相功率高16位
B phase power on the inner side of the grid high _Word
	R
	
	1W
	S16

	702
	电网侧内侧C相功率高16位
C phase power on the inner side of the grid high _Word
	R
	
	1W
	S16

	703
	电网侧-内侧总有功功率 高16位
Total active power from side to side of the grid high _Word
	R
	
	1W
	S16

	704
	电网侧-内侧总视在功率高16位 
Grid side - inside total apparent power high _Word
	R
	
	1W
	预留

	705
	电网外置-功率A高16位
Out-of-grid -power A high _Word
	R
	
	1W
	S16

	706
	电网外置-功率B高16位
Out-of-grid -power B high _Word
	R
	
	1W
	S16

	707
	电网外置-功率C高16位
Out-of-grid -power C high _Word
	R
	
	1W
	S16

	708
	电网外置-总有功功率高16位
Out-of-grid –total power high _Word
	R
	
	1W
	S16

	709
	电网外置-总视在功率高16位
Out-of-grid –total apparent power high _Word
	R
	
	1VA
	S16

	710
	Grid side A phase reactive power。 
	
	
	
	Low byte

	711
	
	
	
	
	High byte

	712
	Grid side B phase reactive power。
	
	
	
	

	713
	
	
	
	
	

	714
	Grid side C phase reactive power。
	
	
	
	

	715
	
	
	
	
	

	
	
	
	
	
	Factory test only
BIT00:
0：CT

1：Meter   
BIT01-BIT15: undefine

	738
	内部风扇返回AD值
	
	
	
	

	739
	外部风扇返回AD值
	
	
	
	

	
	
	
	
	
	

	800
	厂内自检
	R
	
	
	

	
	预留
	
	
	
	


	Customized register

	Addr
	Register meaning
	R/W
	data range
	Unit
	Note

	1000
	Spain_timer1_mode1  
	
	Low Bit0-7
	
	Mon to Fri

Bit0：GM

Bit1：BK

Bit2：PS

Bit3：BF   Battery First

Bit4：Gen Charge EN

	
	Spain_timer2_mode1
	
	High Bit0-7
	
	

	1001
	Spain_timer3_mode1
	
	Low Bit0-7
	
	

	
	Spain_timer4_mode1
	
	High Bit0-7
	
	

	1002
	Spain_timer5_mode1
	
	Low Bit0-7
	
	

	
	Spain_timer6_mode1
	
	High Bit0-7
	
	

	1003
	Spain_timer1_mode2
	
	Low Bit0-7
	
	Sat to Sun

Bit0：GM

Bit1：BK

Bit2：PS

Bit3：BF   Battery First

	
	Spain_timer2_mode2
	
	High Bit0-7
	
	

	1004
	Spain_timer3_mode2
	
	Low Bit0-7
	
	

	
	Spain_timer4_mode2
	
	High Bit0-7
	
	

	1005
	Spain_timer5_mode2
	
	Low Bit0-7
	
	

	
	Spain_timer6_mode2
	
	High Bit0-7
	
	

	1006
	SOC2-1    MON TO FRI
	
	0-100%
	
	

	1007
	SOC2-2
	
	
	
	

	
	SOC2-3
	
	
	
	

	
	SOC2-4
	
	
	
	

	
	SOC2-5
	
	
	
	

	
	SOC2-6
	
	
	
	

	1012
	SOC2-1    SAT TO SUN
	
	
	
	

	1013
	SOC2-2
	
	
	
	

	1014
	SOC2-3
	
	
	
	

	1015
	SOC2-4
	
	
	
	

	1016
	SOC2-5
	
	
	
	

	1017
	SOC2-6
	
	
	
	

	1018
	SOC3-1    MON TO FRI
	
	
	     
	

	
	SOC3-2
	
	
	
	

	
	SOC3-3
	
	
	
	

	
	SOC3-4
	
	
	
	

	
	SOC3-5
	
	
	
	

	
	SOC3-6
	
	
	
	

	1024
	SOC3-1    SAT TO SUN
	
	
	
	

	
	SOC3-2
	
	
	
	

	
	SOC3-3
	
	
	
	

	
	SOC3-4
	
	
	
	

	
	SOC3-5
	
	
	
	

	
	SOC3-6
	
	
	
	

	1030
	GPS-1     MON TO FRI
	
	0-xxRated
	10W
	

	
	GPS-2
	
	
	
	

	
	GPS-3
	
	
	
	

	
	GPS-4
	
	
	
	

	
	GPS-5
	
	
	
	

	
	GPS-6
	
	
	
	

	1036
	GPS-1     SAT TO SUN
	
	
	
	

	1037
	GPS-2
	
	
	
	

	1038
	GPS-3
	
	
	
	

	1039
	GPS-4
	
	
	
	

	1040
	GPS-5
	
	
	
	

	1041
	GPS-6
	
	
	
	

	1042
	Mode Time1
	
	
	
	

	1043
	Mode Time2
	
	
	
	

	1044
	Mode Time3
	
	
	
	

	1045
	Mode Time4
	
	
	
	

	1046
	Mode Time5
	
	
	
	

	1047
	Mode Time6
	
	
	
	

	1048
	Gen_charge FG
	
	
	
	Bit0  time1 gen charge EN

Bit1  time2 gen charge EN

Bit2  time3 gen charge EN

Bit3  time4 gen charge EN

Bit4  time5 gen charge EN

Bit5  time6 gen charge EN

	1049
	GEN charge ON value
	
	
	
	

	1050
	GEN charge OFF value
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	1100
	Remote mode
	R/W
	
	
	0:disable  1: enable

	1101
	Remote mode watch dog time
	R/W
	[10,18000]
	S
	 0xFFFF: mean watch dog off [default value]

If watch dog out of this setting vaule, inv will exit remote mode

	
	
	
	
	
	

	1106
	AC power control mode
	R/W
	
	
	0:control three pahse together

1: each phase independent

	
	
	
	
	
	

	
	
	
	
	
	

	1111
	setting INV output power, ABC 3 phase
	R/W
	[-1200,1200]
	0.1%
	

	1112
	setting INV output power, A phase
	R/W
	[-1200,1200]
	0.1%
	

	1113
	setting INV output power, B phase
	R/W
	[-1200,1200]
	0.1%
	

	1114
	setting INV output power, C phase
	R/W
	[-1200,1200]
	0.1%
	

	
	
	
	
	
	

	1117
	Reactive power mode
	
	
	
	0: off

1,PF mode

2,Var  %

	1118
	Setting reactive vaule 3phase
	R/W
	[-800,+800]

[-1200,+1200]
	PF:

VAR:0.1%
	PF:  -800   -0.8

     -990   -0.99

     1000   1

     999    0.99

     800    0.8

	1119
	Setting reactive vaule Aphase
	R/W
	
	
	

	1120
	Setting reactive vaule Bphase
	R/W
	
	
	

	1121
	Setting reactive vaule Cphase
	R/W
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	


03德业电池只读区

	Addr.
	寄存器含义
	R/W
	Range
	Unit
	note

	德业电池

	10000
	设备类型

Device Type
	R
	
	
	0x700:锂电池Pack协议

	10001
	协议版本号

Protocol Version
	R
	
	
	

	10002
	电池PackNum数
Packnum number
	R
	
	1
	

	10003
	电池电压

Battery voltage
	R
	
	0.1V
	

	10004
	电池电流

Battery current
	R
	
	0.1A
	

	10005
	电池容量SOC

Battery SOC
	R
	
	1%
	

	10006
	电池健康度SOH

Battery SOH
	R
	
	1%
	

	10007
	电池剩余容量

Battery CApAH
	R
	
	1AH
	

	10008
	电池温度

Battery Temp
	R
	
	0.1C
	

	10009
	电池充电电压

Charge Voltage
	R
	
	0.1V
	

	10010
	电池放电电压

Discharge voltage
	R
	
	0.1V
	

	10011
	电池充电截止电压

Charge End voltage
	R
	
	1V
	

	10012
	电池放电截止电压

Discharge End voltage
	R
	
	1V
	

	10013
	电池充电限流

Charge limit current
	R
	
	1A
	

	10014
	电池放电限流

Discharge limit current
	R
	
	1A
	

	10015
	电池离网充电限流

Off grid Charge limit current
	R
	
	1A
	

	10016
	电池离网放电电流

Off grid Discharge limit current
	R
	
	1A
	

	10017
	强充标志
Force Charge Flag
	R
	
	
	

	10018
	校准容量标志

Check SOC Flag
	R
	
	
	

	10019
	电池故障1
Battery Fault1
	R
	
	
	

	10020
	电池故障2
Battery Fault2
	R
	
	
	

	10021
	电池告警1
Battery Alarm1
	R
	
	
	

	10022
	电池告警2

Battery Alarm2
	R
	
	
	

	10023
	预留1
	R
	
	
	

	10024
	预留2
	R
	
	
	

	10025
	预留3
	R
	
	
	

	10026
	预留4
	R
	
	
	

	10027
	预留5
	R
	
	
	

	10028
	预留6
	R
	
	
	

	10029
	预留7
	R
	
	
	

	10030
	预留8
	R
	
	
	

	10031
	预留9
	
	
	
	

	10032
	1号1字节
	R
	‘0’- ‘9’ ‘A’- ‘Z’
	
	ASCII字符

	
	1号2字节
	
	
	
	

	10033
	1号3字节
	R
	‘0’- ‘9’ ‘A’- ‘Z’
	
	ASCII字符

	
	1号4字节
	
	
	
	

	10034
	1号5字节
	R
	‘0’- ‘9’ ‘A’- ‘Z’
	
	ASCII字符

	
	1号6字节
	
	
	
	

	10035
	1号7字节
	R
	‘0’- ‘9’ ‘A’- ‘Z’
	
	ASCII字符

	
	1号8字节
	
	
	
	

	10036
	1号9字节
	R
	‘0’- ‘9’ ‘A’- ‘Z’
	
	ASCII字符

	
	1号10字节
	
	
	
	

	10037
	1号11字节
	R
	‘0’- ‘9’ ‘A’- ‘Z’
	
	ASCII字符

	
	1号12字节
	
	
	
	

	10038
	1号13字节
	R
	‘0’- ‘9’ ‘A’- ‘Z’
	
	ASCII字符

	
	1号14字节
	
	
	
	

	10039
	1号15字节
	R
	‘0’- ‘9’ ‘A’- ‘Z’
	
	ASCII字符


	10040
	PACK1
	Module Voltage
	
	
	0.01V
	

	10041
	
	Module Current
	
	
	0.1A
	

	10042
	
	Temperate-AVE
	
	
	
	1250 mean 25.0℃

	10043
	
	Temperate-CellMax
	
	
	
	1250 mean 25.0℃

	10044
	
	Temperate-CellMin
	
	
	
	1250 mean 25.0℃

	10045
	
	Temperate-MosMax
	
	
	
	1250 mean 25.0℃

	10046
	
	Temperate-HeatMem
	
	
	
	1250 mean 25.0℃

	10047
	
	SOC
	
	
	0.1
	

	10048
	
	SOH
	
	
	0.1
	

	10049
	
	Remain Capacity
	
	
	0.1AH
	

	10050
	
	Total Capacity
	
	
	0.1AH
	

	10051
	
	Charge Voltage
	
	
	0.01V
	

	10052
	
	Charge Current
	
	
	0.1A
	

	10053
	
	Discharge Current
	
	
	0.1A
	

	10054
	
	Max Cell V 
	
	
	0.01V
	

	10055
	
	Min Cell V
	
	
	0.01V
	

	10056
	
	Cycle number
	
	
	1
	

	10057
	
	MOS Status
	
	
	1
	

	10058
	
	Warming1
	
	
	--
	

	10059
	
	Warming2
	
	
	--
	

	10060
	
	Fault1
	
	
	--
	

	10061
	
	Fault2
	
	
	--
	

	10062
	
	软件版本号
	
	
	--
	

	10063
	
	硬件版本号
	
	
	--
	

	10064
	
	预留1
	
	
	
	

	10065
	
	预留2
	
	
	
	

	10066
	
	预留3
	
	
	
	

	10067
	
	预留4
	
	
	
	

	10068
	
	预留5
	
	
	
	

	10069
	
	预留6
	
	
	
	

	以此类推8个寄存器的SN+22和数据寄存器=30个寄存器为第二个电池包信息

	以此类推8个寄存器的SN+22和数据寄存器=30个寄存器为第三个电池包信息


德业语言包协议
	Addr.

	寄存器含义
	R/W
	Range
	Unit
	note

	德业语言包

	20000
	语言协议版本号
Language Type version
	R
	
	
	

	20001
	语言类型数量
Language Type number
	R
	[0-200]
	
	

	20002
	语言类型
Language Type
	R
	
	
	1：德语
2：西班牙语
3：匈牙利语
4：意大利语
（语言序号需要和液晶中的对齐）

	20003
	语言版本号
Language Version
	R
	
	
	

	20004
	语言类型
Language Type
	R
	
	1
	1：德语
2：西班牙语
3：匈牙利语
4：意大利语
（语言序号需要和液晶中的对齐）

	20005
	语言版本号
Language Version
	R
	
	0.1V
	

	20006
	语言类型
Language Type
	R
	
	0.1A
	1：德语
2：西班牙语
3：匈牙利语
4：意大利语
（语言序号需要和液晶中的对齐）

	20007
	语言版本号
Language Version
	R
	
	1%
	

	20008
	语言类型
Language Type
	R
	
	1%
	1：德语
2：西班牙语
3：匈牙利语
4：意大利语
（语言序号需要和液晶中的对齐）

	20009
	语言版本号
Language Version
	R
	
	1AH
	

	20010
	语言类型
Language Type
	R
	
	1%
	1：德语
2：西班牙语
3：匈牙利语
4：意大利语
（语言序号需要和液晶中的对齐）

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	


内存记录表

	内存记录表

	Addr.
	寄存器含义
	R/W
	Range
	Unit
	note

	1000
	逆变器故障信息
	R
	
	
	长度范围是500

	……
	
	R
	
	
	

	……
	
	R
	
	
	

	1499
	
	R
	
	
	

	
	
	
	
	
	


故障代码

告警代码

	Error code 
	Description /描述
	Solutions/解决方案

	
	
	

	
	
	

	W01
	reserve
	

	W02
	FAN_WARN
	

	W03
	Grid phase wrong
	

	W04
	meter_Comm_Fail
	


故障代码：Fault Code
	Error code 
	Description /描述
	Solutions/解决方案

	F07
	DC/DC_Softsart_Fault

DC/DC软起故障
	DC/DC softstart fault
1. Check the battery fuse;
2. Restart and check whether it is in normal;
3. Seek help from us, if can’t go back to noarmal state

	F10
	AuxPowerBoard_Failure

辅助电源故障
	Auxiliary power supply failure
1. Wait for minutes then check;
2. Remove wifi plug or other communicator;
3. Seek help from us, if can’t go back to noarmal state

	F13 
	Working mode change

模式切换
	Inverter work mode changed
1. wait for a minute and check;
2. Seek help from us, if can't go back to normal state.

	F18 
	AC over current fault
of hardware

硬件交流过流
	AC side over current fault
1. Please check whether the backup load power and common
load power are within the range;
2. Restart and check whether it is in normal;
3. Seek help from us, if can not go back to normal state.

	F20 
	DC over current fault of
the hardware

硬件直流过流
	DC side over current fault
1. Check PV module connect and battery connect;
2. Turn off the DC switch and AC switch and then wait one
minute,then turn on the DC/AC switch again;
3. Seek help from us, if can not go back to normal state.

	F22
	Tz_EmergSStop_Fault

急停故障（逆变器被锁定）
	Tz_EmergSStop_Fault                                                                      Seek help from us,This failure hardly happens.



	F23 
	AC leakage current is
transient over current

瞬时漏电流故障
	Leakage current fault
1. Check the cable of PV module and inverter;
2. Restart inverter;
3. Seek help from us, if can not go back to normal state.

	F24 
	DC insulation impedance
failure

方阵绝缘阻抗故障
	PV isolation resistance is too low
1. Check the connection of PV panels and inverter is firmly and
correctly;
2. Check whether the PE cable of inverter is connected to ground;
3. Seek help from us, if can not go back to normal state.

	F26 
	The DC busbar is
unbalanced

直流母线不平衡
	1. Please wait for a while and check whether it is normal;
2. If still same, and turn off the DC switch and AC switch and
wait for one minute and then turn on the DC/AC switch;
3. Seek help from us, if can not go back to normal state.

	F29
	Parallel_CANBus_Fault

并联通讯故障
	This fualt only for inverters working in parallel mode
1. Check the parallel setting according to the instructions;
2. Check  the connection of the CANBus;
3. Seek help from us

	F35 
	No AC grid

无市电
	No Utility
1. Please confirm grid is lost or not;
2. Check the grid connection is good or not;
3. Check the switch between inverter and grid is on or not;
4. Seek help from us, if can not go back to normal state.

	F41
	Parallel_system_Stop

并联系统停机故障
	In parallel system,due to other inverter faults.
1. Wait for minutes then check all inverters in this parallel system;
2. If inverter can’t go back to normal state, record fault codes of all inverters, then seek help from us.

	F42 
	AC line low voltage

线电压过低故障
	Grid voltage fault
1. Check the AC voltage is in the range of standard voltage in
specification;
2. Check whether grid AC cables are firmly and correctly
connected;
3. Seek help from us, if can not go back to normal state.

	F46/F49
	Bcakup_Battery_Fault

备份电池故障
	Backup battery fault.  
1. Check the battery capacity;
2. Check the connection between batteries and inverters;
3. If inverter can’t go back to normal after load reduction, seek help from us

	F47 
	AC over frequency

交流过频
	Grid frequency out of range
1. Check the frequency is in the range of specification or not;
2. Check whether AC cables are firmly and correctly connected;
3. Seek help from us, if can not go back to normal state.

	F48 
	AC lower frequency

交流欠频
	Grid frequency out of range
1. Check the frequency is in the range of specification or not;
2. Check whether AC cables are firmly and correctly connected;
3. Seek help from us, if can not go back to normal state.

	F56 
	DC busbar voltage is
too low

母线电压过低
	Battery voltage low
1. Check whether battery voltage is too low;
2. If the battery voltage is too low, using PV or grid to charge the
battery;
3. Seek help from us, if can not go back to normal state.

	F58
	BMS communication fault
BMS通讯故障
	

	F62
	DRM检测
	Check whether the DRM function is enabled by mistake.

Check whether the DRM cable is damaged

	F63 
	ARC fault

拉弧故障
	1. ARC fault detection is only for US market;
2. Check PV module cable connection and clear the fault;
3. Seek help from us, if can not go back to normal state.

	F64 
	Heat sink high temperature
failure

散热器温度过高
	Heat sink temperature is too high
1. Check whether the work environment temperature is too high;
2. Turn off the inverter for 10mins and restart;
3. Seek help from us, if can not go back to normal state.


附录

附录一：额定功率机型选择表

	
	三相低压
	高压A系列15kw（1200V）
	高压A系列15kw（650V）
	高压D系列5-10kw
	高压B系列50kw（1200V）
	高压B系列50kw

（650V）

	0
	默认12kw
	默认15kw
	默认15kw
	默认10kw
	默认50kw
	默认30KW

	1
	10kw
	12kw
	10kw
	
	40kw
	25kw

	2
	8kw
	10kw
	8kw
	
	30kw
	20kw

	3
	6kw
	8kw
	
	
	35kw
	

	4
	5kw
	20kw
	
	
	60KW(US)
	

	5
	14kw
	25kw
	
	
	80KW
	

	6
	15kw
	
	
	
	29.9KW
	

	7
	16kw
	
	
	
	
	

	8
	18kw
	
	
	
	
	

	9
	20kw
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	


附录二：机器系列区分表

	
	三相低压
	三相高压

	A
	NULL
	6-25kw系列外壳

	B
	NULL
	30-50kw系列外壳

	C
	
	A系列的一体机

	D
	
	5-10kw系列

	
	
	


附录三：输出电压选择表

	
	三相低压
	三相高压650V
	三相高压1200V

	0
	LN:220VAC LL:380VAC
	LN:120VAC LL:208VAC
	LN:220VAC LL:380VAC

	1
	LN:230VAC LL:398VAC
	LN:115VAC LL:200VAC
	LN:230VAC LL:400VAC

	2
	LN:240VAC LL:415VAC
	LN:133VAC LL:230VAC
	LN:277VAC LL:480VAC

	3
	LN:120VAC LL:208VAC
	LN:127VAC LL:220VAC
	LN:127VAC LL:220VAC

	4
	LN:133VAC LL:220VAC
	
	

	5
	LN:115VAC LL:200VAC
	
	


附录四:电网安规选择表

	
	电网安规名
	

	0
	NOMAL
	

	1
	IEEE1547
	

	2
	RULE21,                 
	

	3
	SRD_UL1741,             
	

	4
	CEI_0_21_Internal,      
	Italy <11.9kw

	5
	EN50549_CZ,             
	Czech >16A

	6
	AS4777_A,               
	

	7
	AS4777_B,               
	

	8
	AS4777_C,               
	

	9
	AS4777_NewZealand,     
	

	10
	VDE4105,                
	Germany  

	11
	OVE_Directive_R25,     
	Austria奥地利

	12
	EN50549_CZ_PPDS_L16A,  
	Czech <16A

	13
	NRS097,                 
	South Africa

	14
	G98,                    
	

	15
	G99,                    
	

	16
	EN50549_1_Norway_133V,  
	Norway-133

	17
	EN50549_1_Norway_230V,  
	Norway-230

	18
	JAPAN_200VAC,       
	Japan-200VAC

	19
	CEI_0_21_External,       
	Italy >11.9kw

	20
	CEI_0_21_Areti,        
	Italy Rome

	21
	JAPAN_400VAC_3P3W,      
	Japan-400VAC

	22
	JAPAN_415VAC_3P4W       
	Japan-415VAC

	23
	EN 50549-1-Switzerland
	Switzerland

	
	
	


附录五：

                                                                      第 39 页  共 48 页


