## Sheet1
BMS Sunny Island OnGrid
序号 | name | 数值 | 单位 |  | 功能开关（function switch）
1 | Alarm-Monomer high voltage | 3.48 | V | When charging, the monomer cell reaches the warning value. The upper machine will prompt warning and do not stop charging | Voltage sensing failure | ON | This function is not used temporarily
2 | Recovery-Monomer high voltage | 3.4 | V | Remove the high voltage warning recovery value of monomer cell | Temperature sensing failure | ON | NTC open circuit, short circuit
3 | Alarm-Monomer low voltage | 3.1 | V | When discharging, the monomer cell reaches the warning value. The upper machine will prompt warning and do not stop charging | Current sensing failure | ON | This function is not used temporarily
4 | Recovery-Monomer low voltage | 3.2 | V | Remove the low voltage warning recovery value of monomer cell | Key switch failure | ON | The reset button is stuck all the time, and the BMS will prompt the failure
5 | Monomer overvoltage protection | 3.65 | V | When charging, the monomer cell reaches the protect value. The upper machine will prompt protect and stop charging | Cell differential failure | ON | The pressure difference between the cells is large, indicating failure
6 | Overvoltage monomer recovery | 3.4 | V | Remove the over voltage warning recovery value of monomer cell | Charging switch failure | ON | This function is not used temporarily
7 | Monomer undervoltage protection | 2.7 | V | When discharging, the monomer cell reaches the protect value. The upper machine will prompt protect and stop charging | Discharge switch failure | ON | This function is not used temporarily
8 | Undervoltage monomer recovery | 3.1 | V | Remove the under voltage warning recovery value of monomer cell | Current limiting switch failed | ON | This function is not used temporarily
9 | Balanced turn-on voltage | 3.4 | V | Monomer cell meets the requirements of turning on voltage | Alarm - Monomer high voltage | ON | Single cell high alarm during charging
10 | Low - voltage charge suppression of the cell | 1.5 | V | Cell voltage is too low to charge | Monomer overvoltage protection | ON | During charging, the monomer battery cell is over-protected and stops charging
11 | Alarm - High total voltage | 55.2 | V | When charging, the total pressure voltage reaches the warning value. The upper machine will prompt warning and do not stop charging | Alarm - Monomer low voltage | OFF | Low warning of monomer cell during discharge
12 | Recovery - High total voltage | 54 | V | Remove the total pressure high voltage warning recovery value of monomer cell | Monomer undervoltage protection | ON | During discharging, the monomer battery cell is under-protected and stops discharging
13 | Alarm - Low total voltage | 46.4 | V | When discharging, the total pressure voltage reaches the warning value. The upper machine will prompt warning and do not stop charging | Alarm - High total voltage | ON | High warning of total cell during charge
14 | Recovery - Low total voltage | 48 | V | Remove the total pressure low voltage warning recovery value of monomer cell | Total_voltage overvoltage protection | OFF | During charging, the total battery cell is over-protected and stops charging
15 | Total_voltage overvoltage protection | 55.8 | V | When charging, the total pressure voltage reaches the protect value. The upper machine will prompt protect and stop charging | Alarm - Low total voltage | ON | Low warning of total cell during discharge
16 | Overvoltage Total_voltage recovery | 54 | V | Remove the total pressure overvoltage protection recovery value | Total_voltage undervoltage protection | ON | During discharging, the total battery cell is under-protected and stops discharging
17 | Total_voltage undervoltage protection | 43.2 | V | When discharging, the total pressure voltage reaches the protect value. The upper machine will prompt protect and stop charging | Alarm - High temperature charging | ON | Warning of high cell temperature during charging
18 | Undervoltage Total_voltage recovery | 48 | V | Remove the total pressure undervoltage protection recovery value | Protect - Over temperature charging | ON | During charging, the battery cell is over-protected and stops charging
19 | Overcharge protection | 63 | V | BMS detects the charger voltage is too high, implements charging protection and stops charging | Alarm - Low temperature charging | ON | Warning of low cell temperature during charging
20 | Recovery of overvoltage | 61 | V | BMS detects the charger voltage reaches the protection recovery value | Protect - Under temperature charging | ON | During charging, the battery cell is over-protected and stops charging
21 | Alarm - High temperature charging | 50 | ℃ | When charging,the cell temperature reaches the high temperature warning value. The upper machine will prompt warning and do not stop charging | Alarm - High temperature discharging | ON | High cell temperature warning during discharge
22 | Recovery - High temperature charging | 47 | ℃ | Remove the cell high temperature warning recovery value of cell | Protect - Over temperature discharging | ON | When discharging, the temperature of the electric cell is over protected and the discharge is stopped
23 | Alarm - Low temperature charging | 2 | ℃ | When charging,the cell temperature reaches the low temperature warning value. The upper machine will prompt warning and do not stop charging | Alarm - Low temperature discharging | ON | Low cell temperature warning during discharge
24 | Recovery - Low temperature charging | 5 | ℃ | Remove the cell low temperature warning recovery value of cell | Protect - Under temperature discharging | ON | When discharging, the temperature of the electric cell is under protected and the discharge is stopped
25 | Protect - Over temperature charging | 55 | ℃ | When charging,the cell temperature reaches the over temperature warning value. The upper machine will prompt warning and stop charging | Ambient high temperature alarm | ON | Warning when the ambient temperature reaches high
26 | Recovery - Over temperature charging | 50 | ℃ | Remove the recovery value of cell temperature over-temperature protection | Protect - Ambient over-temperature | ON | Stop charging and discharging when the ambient temperature reaches over-protection
27 | Protect - Under temperature charging | -10 | ℃ | When charging,the cell temperature reaches the under temperature protect value. The upper machine will prompt protect and stop charging | Ambient low temperature alarm | ON | Low ambient temperature warning
28 | Recovery - Under temperature charging | 0 | ℃ | Remove the recovery value of cell temperature undertemperature protection | Protect - Ambient low-temperature | ON | Stop charging and discharging when the ambient temperature reaches under-protection
29 | Alarm - High temperature discharging | 52 | ℃ | When discharging,the cell temperature reaches the high temperature protect value. The upper machine will prompt protect and do not stop charging | Protect - Power over-temperature | ON | Stop charging and discharging when the power temperature reaches over-protection
30 | Recovery - High temperature discharging | 47 | ℃ | Remove the recovery value of cell temperature high temperature protection | Power high temperature alarm | ON | High power temperature warning
31 | Alarm - Low temperature discharging | -10 | ℃ | When discharging,the cell temperature reaches the low temperature protect value. The upper machine will prompt protect and do not stop charging | Battery low temperature heating | ON | Before turning on this function, you must confirm whether the hardware meets the requirements. Default without heating hardware
32 | Recovery - Low temperature discharging | 3 | ℃ | Remove the recovery value of cell temperature low temperature protection | Secondary tripping protection | ON | Before turning on this function, you must confirm whether the hardware meets the requirements. Default without secondary tripping hardware
33 | Protect - Over temperature discharging | 55 | ℃ | When discharging,the cell temperature reaches the overtemperature protect value. The upper machine will prompt protect and stop charging | Alarm - High charging current | ON | Excessive current warning during charging
34 | Recovery - Over temperature discharging | 50 | ℃ | Remove the recovery value of cell temperature over temperature protection | Charge overcurrent protection | ON | During charging, over-current protection, stop charging
35 | Protect - Under temperature discharging | -10 | ℃ | When discharging,the cell temperature reaches the undertemperature protect value. The upper machine will prompt protect and stop charging | Alarm - High discharging current | ON | Excessive current warning during discharging
36 | Recovery - Under temperature discharging | 0 | ℃ | Remove the recovery value of cell temperature under temperature protection | Discharge overcurrent protection | ON | During discharging, over-current protection, stop charging
37 | Battery low temperature heating | 0 | ℃ | When the charger is online and the temperature of the cell is too low to reach the heating temperature, start the heating | Transient current protection | ON | When discharging, the current reaches secondary protection and the discharge stops
38 | Cell heating recovery | 10 | ℃ | Stop heating after the temperature of the cell recovers | Output short circuit protection | ON | The output terminal is short-circuited and the output is closed. 60S automatic recovery or charging release.
39 | Ambient high temperature alarm | 50 | ℃ | When the ambient temperature reaches the high temperature warning value, the upper computer prompts the warning and does not stop charging and discharging | Transient overcurrent locking | OFF | If the secondary protection occurs continuously during the discharge, the BMS will be locked and not recovered. General shutdown
40 | Ambient high temperature recovery | 47 | ℃ | Remove the high temperature warning recovery value | Output short circuit Locking | ON | The BMS will lock and not recover if the output terminal continues to have short circuit protection
41 | Ambient low temperature alarm | 0 | ℃ | When the ambient temperature reaches the low temperature warning value, the upper computer prompts the warning and does not stop charging and discharging | Charging high voltage protection | ON | Charger over-voltage protection
42 | Ambient low temperature recovery | 3 | ℃ | Remove the low temperature warning recovery value | Intermittent power supply function | ON | After charging overvoltage protection, the SOC decreases to the recovery value. Resume charging
43 | Protect - Ambient over-temperature | 60 | ℃ | When the ambient temperature reaches the over temperature warning value, the upper computer prompts the warning and does not stop charging and discharging | Remaining capacity alarm | ON | Low capacity warning
44 | Recovery - Ambient over-temperature | 55 | ℃ | Remove the over temperature warning recovery value | Residual capacity protection | ON | Low capacity protection, closing output
45 | Protect - Ambient low-temperature | -10 | ℃ | When the ambient temperature reaches the under temperature warning value, the upper computer prompts the warning and does not stop charging and discharging | Low - voltage charge suppression of the cell | ON | Do not charge if the battery cell is too low
46 | Recovery - Ambient under-temperature | 0 | ℃ | Remove the under temperature warning recovery value | Output reverse connection protection | OFF | This function is not used temporarily
47 | Power high temperature alarm | 90 | ℃ | When the power temperature reaches the high temperature warning value, the upper computer prompts the warning and does not stop charging and discharging | Output connection failure | OFF | This function is not used temporarily
48 | Power high temperature recovery | 85 | ℃ | Remove the power temperature high temperature warning recovery value | Output soft starting energy | ON | When the output terminal is connected to the device, BMS will pre-charge the device
49 | Protect - Power over-temperature | 100 | ℃ | When the power temperature reaches the over temperature warning value, the upper computer prompts the protect and stop charging and discharging | Charging equalization function | OFF | When charging, when the equalizing opening condition is reached and the pressure difference reaches the condition, the equalizing is started
50 | Recovery - Power over-temperature | 85 | ℃ | Remove the power temperature over temperature protection recovery value | Static balancing function | OFF | In standby, when the equalizing opening condition is reached and the differential pressure reaches the condition, the equalizing is started
51 | Alarm - High charging current | 200 | A | When charging,the current is too large to reach the warning value.The upper machine will prompt warning and do not stop charging. | Timeout forbidden equalization | ON | In standby mode, balance is stopped after a certain time
52 | Recovery - High charging current | 195 | A | Remove the charging overcurrent warning recovery value | Over - temperature equilibrium is forbidden | ON | When the temperature is too high, the BMS is unbalanced. This temperature is based on the ambient temperature alarm value
53 | Alarm - High discharging current | -205 | A | When discharging,the current is too large to reach the warning value.The upper machine will prompt warning and do not stop charging. | Automatic activation charge | ON | After "undervoltage protection" or "residual capacity protection", wait for the setting time of "charging activation interval" to expire, and force the output for 60 seconds to activate the charger. If the charging fails to be activated, turn off the output and continue to wait
54 | Recovery - High discharging current | -203 | A | Remove the discharging overcurrent warning recovery value | Manual activation charging | OFF | After discharging the undervoltage protection, BMS turns off the output. The BMS is forced to activate manually, and the BMS clears the protection status. Generally used for home storage, the inverter can only be charged after detecting the port voltage
55 | Charge overcurrent protection | 210 | A | When charging,the current is too large to reach the protect value.The upper machine will prompt protect and stop charging. | Active current limiting charge | OFF | When this function is turned on, the BMS limits the 10A current regardless of the external current
56 | Discharge overcurrent protection | -210 | A | When discharging,the current is too large to reach the protect value.The upper machine will prompt protect and stop charging. | Passive current limiting charge | ON | When this function is turned on, the charging current reaches the charging over-current alarm, and the BMS starts to limit the current
57 | Transient overcurrent protection | -300 | A | When discharging, the current reaches the secondary protection value, and the upper computer prompts the transient overcurrent protection to stop discharging | Switch off function | ON | Use an external switch to turn on this function, which is a self-locking switch
58 | Output soft start delay | 9000 | mS | When BMS outputs and terminates the equipment, the equipment pulls the battery power, and BMS pre-charges the equipment to prevent short circuit protection | Standby shutdown function | ON | The battery is standby for a long time, and the BMS shuts down and sleeps after reaching a certain time
59 | Battery rated capacity | 302 | Ah | Set the battery rated capacity according to the battery capacity. | Historical recording function | ON | This function is to save the status of BMS or the data of BMS in case of alarm and protection
60 | SOC | 50 | Ah | SOC | LCD Display Function | ON | When this function is turned on, the external LCD display can be connected
61 | Cell failure differential pressure | 0.5 | V | The differential pressure between the cell is large, and BMS will prompt that the differential pressure between the cell is invalid and not protected | Bluetooth communication function | ON | When this function is turned on, the Bluetooth function module is required
62 | Battery failure recovery | 0.3 | V | Remove the recovery value of cell differential pressure failure | Automatic address coding | OFF | When this function is turned on, parallel wiring needs to follow the automatic coding mode
63 | Pressure balanced open | 0.03 | V | Equalization reaches the turning on voltage, and the differential pressure reaches the condition of turning on. | Parallel external polling | OFF | When this function is turned on, the automatic code dialing will be paralleled in the non-host mode
64 | End pressure balanced | 0.02 | V | Unbalance start recovery value | Single BMS 1.0C charging | OFF | When this function is turned on, the charging current requested by the single machine is the charging overcurrent alarm value - 10A when communicating with the inverter
65 | Static equalization time | 10 | 时 | When the BMS is not charged and discharged, the static equalization time exceeds a certain time, and the equalization is stopped | 备注：充放电电压保护、电流保护、温度保护等功能不可关闭，不然BMS不保护。告警功能只是提示使用，关闭不影响性能。
66 | Battery number in series | 16 | 串 | The number of electric cell strings is set according to the use of electric cell
67 | Charge overcurrent delay | 10 | 秒 | When charging, the current is too large to reach the protection condition, and BMS stops charging protection according to the set delay time
68 | Discharge overcurrent delay | 10 | 秒 | When discharging,the current is too large to reach the protect value.BMS stops discharging protection according to the set delay time
69 | Transient overcurrent delay | 30 | mS | When discharging, the current is too large to reach the secondary protection condition, and BMS stops discharging protection according to the set delay time
70 | Overcurrent delay recovery | 60 | 秒 | After BMS overcurrent protection, recover the charge and discharge delay again, and detect the external current after 60s
71 | Number of overcurrent recovery | 5 | 次 | When the BMS has frequent overcurrent protection, the BMS is directly locked for more than a certain number of times and is not allowed to recover
72 | Charge current limit delay | 5 | 分 | This function is only effective when the passive current limiting is enabled. The main reason is that the BMS starts the passive current limiting meeting and detects the external current again after a certain period of time
73 | Charging activation delay | 1 | 分 | This function is only used for home storage. The main reason is that after BMS undervoltage protection, the inverter can not detect the battery output, and the protection status is released by pressing the power button manually
74 | Charge activation interval | 10 | 时 | This function is not used temporarily
75 | Charge activation times | 10 | 次 | This function is not used temporarily
76 | Work record interval | 30 | 分 | BMS saves a piece of historical data for a certain period of time under charging and discharging conditions
77 | Standby recording interval | 240 | 分 | BMS saves a piece of historical data for a certain time in standby mode
78 | Standby shutdown delay | 48 | 时 | When the BMS is in standby mode for a long time, the BMS will enter standby shutdown mode. Enter zero power consumption state
79 | Remaining capacity alarm | 15 | % | If the SOC is lower than the warning value, the upper computer will prompt the warning and will not protect
80 | Residual capacity protection | 5 | % | If the SOC is lower than the protection value, the upper computer will prompt for protection and stop discharging
81 | Interval supplementary capacity | 96 | % | After overvoltage protection, BMS voltage reached the recovery value, and SOC did not meet the conditions. Do not resume charging, if the SOC is lower than the gap recharge capacity and the voltage reaches the recovery value, resume charging
82 | Cumulative circulation capacity | 80 | % | In the case of continuous discharge of BMS, the SOC is discharged by more than 20%, and then transferred to charging. BMS will accumulate the number of cycles
83 | Connection fault impedance | 10 | mΩ | Compensate the impedance between cells
84 | Compensation point 1 position | 9 | 串 | The impedance between the compensation cell and the cell, and the corresponding string number can be set (1-9 sections)
85 | Compensation point 1 impedance | 0 | mΩ | Compensate the impedance between cells
86 | Compensation point 2 position | 13 | 串 | The impedance between the compensation cell and the cell, and the corresponding string number can be set (10-16 sections)
87 | Compensation point 2 impedance | 0 | mΩ | Compensate the impedance between cells