## Cover
Archive Files
Document Number: ZW-YF-JS-PVESS.T12-XY-0.1.1-1.0-201610
File name: MODBUS Communication Protocol
Version: V1.0
Department: R&D
Draft:
Audit:
approve:
Archive date:

## Protocol Description
1. ModBus communication protocol is divided into RTU protocol and ASCII protocol. Our company adopts RTU protocol.
2. Serial port configuration
| Start bit | 1st
| Data bits | 8-bit
| Parity bit | none
| Stop bits | 1st
3. The communication baud rate is9600
4. Read data using 03 function code
5. Write data using10Function code
Data Request: | Address code | 1 byte | System Address
| Function code | 1 byte | 0x03
| Starting address | 2 bytes | Register Address | 0x0000 to 0xFFFF
| Number of registers | 2 bytes | 1-125
| CRC Check | 2 bytes | The lower 8 bits are in front, the higher 8 bits are in the back
Data reply: | Address code | 1 byte | System Address
| Function code | 1 byte | 0x03
| Number of bytes | 1 byte | 2*N
| Register Value | 2*N bytes | 1-125
| CRC Check | 2 bytes | The lower 8 bits are in front, the higher 8 bits are in the back
N: Number of requested registers
Error response: | Address code | 1 byte | System Address
| Function code | 1 byte | 0x03+0x80
| Exception code | 1 byte | 01, 02, 03 or 04
| CRC Check | 2 bytes | The lower 8 bits are in front, the higher 8 bits are in the back
Modify registers: | Address code | 1 byte | System Address
| Function code | 1 byte | 0x10
| Starting address | 2 bytes | Register Address
| Number of registers | 2 bytes | 1-123
| Number of bytes | 1 byte
| Write value 2*N | 2*N bytes
| CRC Check | 2 bytes | The lower 8 bits are in front, the higher 8 bits are in the back
reply | Address code | 1 byte | System Address
| Function code | 1 byte | 0x10
| Starting address | 2 bytes | Register Address
| Number of registers | 2 bytes | 1-123
| CRC Check | 2 bytes | The lower 8 bits are in front, the higher 8 bits are in the back
7. Interface Definition

## data
Inverter unit real-time data
Order | Register Address decimal | Data Type | What the data means | Bytes | R/W | unit |  | Remark | Data Types |  | Table 2-1 Operation mode |  | Table 1-1: Inverter status |  |  | Table 1-3: Switchesstate
0x03 | 0 | Status word 0 | Inverter state | 2 | R |  |  | Table 1-1 |  |  | 0 | Standby |  | 1 | 0 |  | 1 | 0
0x03 | 1 | Status word 1 |  | 2 | R | [5 empty] | 1 | DC voltage source | bit15 |  |  | bit15 | Grid relay closes and supplies power
0x03 | 2 | Status word 2 | Switch Status | 2 | R |  |  | Table 1-3 |  |  | 2 | AC voltage source | bit14 |  |  | bit14 | Inverter voltage source power supply | 10 Stages
0x03 | 3 | Status word 3 |  | 2 | R | [5 empty] | 3 |  | bit13 |  |  | bit13 | Inverter current source power supply | 30 stages
0x03 | 4 | Status word 4 | Grid status | 2 | R |  |  | Table 1-5 |  |  | 4 | Power Control | bit12 | Bus voltage out of range | For debugging | bit12 | Large voltage difference | For debugging
0x03 | 5 | Status word 5 | Output Status | 2 | R |  |  | Table 1-6 |  |  | 5 |  | bit11 | Slow start, not completed | For debugging | bit11 | Generator's relay closes and supplies power
0x03 | 6 | Parameter 0 | Working Mode | 2 | R/W |  |  | Table 2-1 |  |  | 6 | Time-based power control | bit10 | Bus voltage out of range | For debugging | bit10 | AC couple on
0x03 | 7 | Parameter 1 | WIFI communication | 2 | R/W |  |  | 5=WIFI communication normal others=abnormal |  |  | 7 | PQ Run | bit9 |  |  | bit9 | smartload on | off
0x03 | 8 | Parameter 2 | Photovoltaic mode | 2 | R/W |  |  | bit0-0PV1 standby bit1-0PV2 standby |  |  | 8 | Automatic on-grid and off-grid switching power control | bit8 |  |  | bit8
0x03 | 9 | Parameter 3 | Grid-connected power | 2 | R/W | [5 empty] | 9 |  | bit7 | Self-test failed |  | bit7
0x03 | 10 | Parameter 4 |  | 2 | R/W | [5 empty] | 10 | Automatic on-grid and off-grid switching, power control based on time | bit6 |  |  | bit6
0x03 | 11 | Parameter 5 | DC bus reference voltage | 2 | R/W | [7 empty] | bit5 | Phase lock abnormality |  | bit5
0x03 | 12 | Parameter 6 | Battery reference voltage | 2 | R/W | [7 empty] | bit4 | Over temperature |  | bit4
0x03 | 13 | Parameter 7 |  | 2 | R/W | [7 empty] | bit3 | AC hardware overcurrent |  | bit3
0x03 | 14 | Parameter 8 | arc extinction command | 2 | R/W | [7 empty] | bit2 | AC software overcurrent |  | bit2 | Unbalanced operation 3 | For debugging
0x03 | 15 | Parameter 9 | Power on/off command | 2 | R/W | [7 empty] | bit1 | Busbar overvoltage |  | bit1 | Unbalanced operation 2 | For debugging
0x03 | 16 | Parameter 10 |  | 2 | R/W | [7 empty] | bit0 | Abnormal load voltage |  | bit0 | Unbalanced operation 1 | For debugging
0x03 | 17 | Parameter 11 |  | 2 | R/W
0x03 | 18 | Command word 0 |  | 2 | R/W
0x03 | 19 | Command word 1 |  | 2 | R/W
0x03 | 20 | Command word 2 | INV software BOOT version number | 2 | R/W | [5 empty] | Table 2-2 Power on/off commands |  | Table 1-5: Grid status |  |  | Table 1-6: Outputstate
0x03 | 21 | Command word 3 | INV software version low 8 digit minor version | 2 | R/W | [6 empty] | 1 |  | 1 | 0 |  | 1 | 0
0x03 | 22 | Waveform channel 0 |  | 2 | R/W | [5 empty] | bit15 |  | bit15 | Shutdown | Power on | bit15
0x03 | 23 | Waveform channel 1 |  | 2 | R/W | [5 empty] | bit14 |  | bit14 |  |  | bit14 | Communication logo | For debugging
0x03 | 24 | Waveform channel 2 |  | 2 | R/W | [5 empty] | bit13 |  | bit13 | Anti-islanding frequency anomaly | For debugging | bit13 | Communication logo | For debugging
0x03 | 25 | Waveform channel 3 |  | 2 | R/W | [5 empty] | bit12 |  | bit12 |  |  | bit12 | Communication logo | For debugging
0x03 | 26 | Data 0 | Inverter voltage A | 2 | R | 0.1 | V |  | UINT16 |  | bit11 |  | bit11 |  |  | bit11 | Large amplitude difference 1 | For debugging
0x03 | 27 | Data 1 | Inverter voltage B | 2 | R | 0.1 | V |  | UINT16 |  | bit10 |  | bit10 |  |  | bit10 | Large amplitude difference | For debugging
0x03 | 28 | Data 2 | Inverter voltage C | 2 | R | 0.1 | V |  | UINT16 |  | bit9 | bit9-bit8: 1 bypass start 2 bypass shutdown | bit9 |  |  | bit9 | Large phase difference | For debugging
0x03 | 29 | Data 3 | Inverter current A | 2 | R | 0.01 | A |  | UINT16 |  | bit8 |  | bit8 | Quick check abnormality |  | bit8 | Large frequency difference | For debugging
0x03 | 30 | Data 4 | Inverter current B | 2 | R | 0.01 | A |  | UINT16 |  | bit7 |  | bit7 |  |  | bit7 | Large phase difference 1 | For debugging
0x03 | 31 | Data 5 | Inverter current C | 2 | R | 0.01 | A |  | UINT16 |  | bit6 |  | bit6 | Abnormal voltage of phase C |  | bit6 | Large frequency difference 1 | For debugging
0x03 | 32 | Data 6 | Grid voltage A | 2 | R | 0.1 | V |  | UINT16 |  | bit5 | bit5-bit4: 1 unbalanced power on 2 unbalanced power off | bit5 | Abnormal voltage of phase B |  | bit5 | Output undervoltage | For debugging
0x03 | 33 | Data 7 | Grid voltage B | 2 | R | 0.1 | V |  | UINT16 |  | bit4 |  | bit4 | Abnormal voltage of phase A |  | bit4
0x03 | 34 | Data 8 | Grid voltage C | 2 | R | 0.1 | V |  | UINT16 |  | bit3 |  | bit3 |  |  | bit3
0x03 | 35 | Data 9 | Grid current A | 2 | R | 0.01 | A |  | UINT16 |  | bit2 |  | bit2 |  |  | bit2 | Abnormal output amplitude | For debugging
0x03 | 36 | Data 10 | Grid current B | 2 | R | 0.01 | A |  | UINT16 |  | bit1 | bit1-bit0: 1 inverter on, 2 inverter off | bit1 |  |  | bit1 | Abnormal output amplitude | For debugging
0x03 | 37 | Data 11 | Grid current C | 2 | R | 0.01 | A |  | UINT16 |  | bit0 |  | bit0 |  |  | bit0 | Abnormal output frequency | For debugging
0x03 | 38 | Data 12 | Load voltage A | 2 | R | 0.1 | V |  | UINT16
0x03 | 39 | Data 13 | Load voltage B | 2 | R | 0.1 | V |  | UINT16
0x03 | 40 | Data 14 | Load voltage C | 2 | R | 0.1 | V |  | UINT16
0x03 | 41 | Data 15 | Load current A | 2 | R | 0.01 | A |  | UINT16 |  | Table 4-1 Battery operation mode |  | Table 1-1: Bus status |  |  | Table 1-3: Batteries state
0x03 | 42 | Data 16 | Load current B | 2 | R | 0.01 | A |  | UINT16 |  | 0 | Standby |  | 1 | 0 |  | 1 | 0
0x03 | 43 | Data 17 | Load current C | 2 | R | 0.01 | A |  | UINT16 |  | 1 | Power Mode | bit15 |  |  | bit15
0x03 | 44 | Data 18 | Diesel generator voltage A | 2 | R | 0.1 | V |  | UINT16 |  | 2 | High voltage regulation mode | bit14 |  |  | bit14
0x03 | 45 | Data 19 | Diesel generator voltage B | 2 | R | 0.1 | V |  | UINT16 |  | 3 | Low voltage regulation mode | bit13 |  |  | bit13
0x03 | 46 | Data 20 | Diesel generator voltage C | 2 | R | 0.1 | V |  | UINT16 |  |  |  | bit12 | Calibration anomaly |  | bit12 | Equalizing
0x03 | 47 | Data 21 | Diesel generator current A | 2 | R | 0.01 | A |  | UINT16 |  |  |  | bit11 |  |  | bit11 | DC switch available | For debugging
0x03 | 48 | Data 22 | Diesel generator current B | 2 | R | 0.01 | A |  | UINT16 |  |  |  | bit10 |  |  | bit10 | Buck software overcurrent
0x03 | 49 | Data 23 | Diesel generator current C | 2 | R | 0.01 | A |  | UINT16 |  |  |  | bit9 |  |  | bit9
0x03 | 50 | Data 24 | Positive bus voltage | 2 | R | 0.1 | V |  | UINT16 |  |  |  | bit8 |  |  | bit8
0x03 | 51 | Data 25 | Negative bus voltage | 2 | R | 0.1 | V |  | UINT16 |  | Table 4-2 Photovoltaic operation mode |  | bit7 |  |  | bit7 | Busbar low | For debugging
0x03 | 52 | Data 26 | Inverter frequency | 2 | R | 0.01 | Hz |  | INT16 |  | 0 | Standby | bit6 |  |  | bit6 | Voltage bus overvoltage
0x03 | 53 | Data 27 | Grid frequency | 2 | R | 0.01 | Hz |  | INT16 |  | 1 | PV 1 operation mode | bit5 | Bus undervoltage (slow) |  | bit5 | Busbar can work | For debugging
0x03 | 54 | Data 28 | Diesel generator output frequency | 2 | R | 0.01 | Hz |  | INT16 |  | 2 | PV 2 operation mode | bit4 | Busbar overvoltage (slow) |  | bit4
0x03 | 55 | Data 29 |  | 2 | R | [5 empty] | 3 | Photovoltaic 1, 2 operation mode | bit3 |  |  | bit3 | Hardware overcurrent
0x03 | 56 | Data 30 | Maximum temperature | 2 | R | 0.1 | °C |  | UINT16 |  |  |  | bit2 |  |  | bit2 | Battery software overcurrent
0x03 | 57 | Data 31 | Inverter working stage | 2 | R |  |  |  | UINT16 |  |  |  | bit1 | Bus undervoltage (fast) |  | bit1 | Battery overvoltage
0x03 | 58 | Data 32 | External CT power A | 2 | R | 0.01 | A |  | UINT16 |  |  |  | bit0 | Busbar overvoltage (fast) |  | bit0 | Battery undervoltage
0x03 | 59 | Data 33 | External CT power B | 2 | R | 0.01 | A |  | UINT16
0x03 | 60 | Data 34 | External CT power C | 2 | R | 0.01 | A |  | UINT16
0x03 | 61 | Data 35 | External CT current A | 2 | R | 0.01 | A |  | UINT16
0x03 | 62 | Data 36 | External CT current B | 2 | R | 0.01 | A |  | UINT16
0x03 | 63 | Data 37 | External CT current C | 2 | R | 0.01 | A |  | UINT16 |  | Table 4-3 Power on/off commands |  | Table 1-5: Photovoltaic status |  |  | Table 1-4: Operation state
0x03 | 64 | Data 38 | Unbalanced current A | 2 | R | 0.01 | A |  | UINT16 |  |  | 1 |  | 1 | 0 |  | 1 | 0
0x03 | 65 | Data 39 | Inverter active power A | 2 | R | 1 | W |  | INT16 |  | bit15 |  | bit15 |  |  | bit15
0x03 | 66 | Data 40 | Inverter active power B | 2 | R | 1 | W |  | INT16 |  | bit14 |  | bit14 |  |  | bit14
0x03 | 67 | Data 41 | Inverter active power C | 2 | R | 1 | W |  | INT16 |  | bit13 |  | bit13 |  |  | bit13 | The battery enters the operation stage
0x03 | 68 | Data 42 | Inverter reactive power A | 2 | R | 1 | Var |  | INT16 |  | bit12 |  | bit12 | Photovoltaic 2 overvoltage |  | bit12 | Battery enters preparation stage
0x03 | 69 | Data 43 | Inverter reactive power B | 2 | R | 1 | Var |  | INT16 |  | bit11 |  | bit11 |  |  | bit11
0x03 | 70 | Data 44 | Inverter reactive power C | 2 | R | 1 | Var |  | INT16 |  | bit10 |  | bit10 | Photovoltaic 2 software overcurrent |  | bit10 | For debugging
0x03 | 71 | Data 45 | UPS active power A | 2 | R | 1 | W | Positive means energy flows to the load | INT16 | UPS LOAD | bit9 | bit9-bit8: 1: PV 2 on 2: PV 2 off | bit9 |  |  | bit9 | For debugging
0x03 | 72 | Data 46 | UPS active power B | 2 | R | 1 | W |  | INT16 |  | bit8 |  | bit8 | PV 1 undervoltage |  | bit8 | For debugging
0x03 | 73 | Data 47 | UPS active power C | 2 | R | 1 | W |  | INT16 |  | bit7 |  | bit7 |  |  | bit7
0x03 | 74 | Data 48 | SMARTLOAD active power A | 2 | R | 1 | Var | Positive means energy flows to the load | INT16 | SMART LOAD | bit6 |  | bit6 |  |  | bit6
0x03 | 75 | Data 49 | SMARTLOAD active power B | 2 | R | 1 | Var |  | INT16 |  | bit5 | bit5-bit4: 1: PV 1 on 2: PV 1 off | bit5 |  |  | bit5 | DC start-up completed
0x03 | 76 | Data 50 | SMARTLOAD active power C | 2 | R | 1 | Var |  | INT16 |  | bit4 |  | bit4 | Photovoltaic 1 overvoltage |  | bit4 | DC starting
0x03 | 77 | Data 51 | Grid active power A | 2 | R | 1 | W | Positive means buying electricity from the grid, negative means selling electricity to the grid | INT16 |  | bit3 |  | bit3 | Photovoltaic hardware current limiting |  | bit3
0x03 | 78 | Data 52 | Grid active power B | 2 | R | 1 | W |  | INT16 |  | bit2 |  | bit2 | Photovoltaic 1 software overcurrent |  | bit2
0x03 | 79 | Data 53 | Grid active power C | 2 | R | 1 | W |  | INT16 |  | bit1 | bit1-bit0: 1: Battery powered on 2: Battery powered off | bit1 |  |  | bit1 | Photovoltaic 2 enters the operation stage
0x03 | 80 | Data 54 | Grid reactive power A | 2 | R | 1 | Var |  | INT16 |  | bit0 |  | bit0 | PV 1 undervoltage |  | bit0 | Photovoltaic 1 enters the operation stage
0x03 | 81 | Data 55 | Grid reactive power B | 2 | R | 1 | Var |  | INT16
0x03 | 82 | Data 56 | Grid reactive power C | 2 | R | 1 | Var |  | INT16
0x03 | 83 | Data 57 | Diesel generator active power A | 2 | R | 1 | W | In generator mode, energy only flows from the generator to the inverter. This value is always positive. | INT16
0x03 | 84 | Data 58 | Diesel generator active power B | 2 | R | 1 | W |  | INT16
0x03 | 85 | Data 59 | Diesel generator active power C | 2 | R | 1 | W |  | INT16
0x03 | 86 | Data 60 | Load active power A | 2 | R | 1 | Var | Positive means energy flows to the load | INT16 | HOME LOAD
0x03 | 87 | Data 61 | Load active power B | 2 | R | 1 | Var |  | INT16
0x03 | 88 | Data 62 | Load active power C | 2 | R | 1 | Var |  | INT16
0x03 | 89 | Data 63 | INV software version 16-bit large version | 2 | R |  |  |  | UINT16
0x03 | 90 | Module online status |  | 2 | R
DC unit real-time data
Order | Register Address | Data Type | What the data means | Bytes | R/W | unit |  | Remark
0x03 | 2000 | Status word 0 | Bus status | 2 | R |  |  | Table 3-1 |  |  | Table 10 Machine operation status |  | Table 1-5:SOCstate
0x03 | 2001 | Status word 1 |  | 2 | R | [8 empty] | 1 | 0
0x03 | 2002 | Status word 2 | Battery Status | 2 | R |  |  | Table 3-3 |  |  | bit15 | reserve | bit15 | Charging Enable
0x03 | 2003 | Status word 3 | Running status | 2 | R |  |  | Table 3-4 |  |  | bit14 | reserve | bit14 | Discharge Enable
0x03 | 2004 | Status word 4 | Photovoltaic status | 2 | R |  |  | Table 3-5 |  |  | bit13 | reserve | bit13
0x03 | 2005 | Status word 5 | Fault status word | 2 | R | [5 empty] | bit12 | reserve | bit12
0x03 | 2006 | Parameter 0 | Battery working mode | 2 | R/W |  |  | Table 4-1 |  |  | bit11 | reserve | bit11
0x03 | 2007 | Parameter 1 | Photovoltaic mode | 2 | R/W |  |  | Table 4-2 |  |  | bit10 | reserve | bit10
0x03 | 2008 | Parameter 2 | Photovoltaic parallel control word | 2 | R/W | [5 empty] | bit9 | reserve | bit9
0x03 | 2009 | Parameter 3 | BMS maximum charging current | 2 | R/W |  |  | 0-3000 |  |  | bit8 | reserve | bit8 | Communication with BMS is normal
0x03 | 2010 | Parameter 4 | BMS maximum discharge current | 2 | R/W |  |  | 0-3000 |  |  | bit7 | 0 = Standby1= Self-Test2= normal3= Alerts4= Fault5= Shutdown | bit7 | SOC value
0x03 | 2011 | Parameter 5 | Bus reference voltage | 2 | R/W | 0.1 | V |  |  |  | bit6 |  | bit6
0x03 | 2012 | Parameter 6 | Battery reference voltage | 2 | R/W | 0.01 | V |  |  |  | bit5 |  | bit5
0x03 | 2013 | Parameter 7 | DC control word | 2 | R/W | [5 empty] | bit4 |  | bit4
0x03 | 2014 | Parameter 8 | BMS Status/BMS SOC | 2 | R/W |  |  | High 8-bit status word/low 8-bit SOC |  |  | bit3 |  | bit3
0x03 | 2015 | Parameter 9 | Power on/off command | 2 | R/W |  |  | Table 4-2 |  |  | bit2 |  | bit2
0x03 | 2016 | Parameter 10 | BMS charging maximum voltage | 2 | R/W | 0.01 | V | 4600-6000 |  |  | bit1 |  | bit1
0x03 | 2017 | Parameter 11 | BMS minimum discharge voltage | 2 | R/W | 0.01 | V | 4000-5400 |  |  | bit0 |  | bit0
0x03 | 2018 | Command word 0 | Record Clearance | 2 | R/W |  |  | 1 = Clearing energy 10 = Clearing in progress 0 = Clearing completed 2 = Clearing events 20 = Clearing in progress 0 = Clearing completed
0x03 | 2019 | Command word 1 | HMI communication address | 2 | R/W |  |  | 1-64
0x03 | 2020 | Command word 2 | Record page number | 2 | R/W |  |  | 1-100
0x03 | 2021 | Command word 3 | Restore factory settings and T1 mark | 2 | R/W |  |  | 1 = Restore factory settings 2 = Mark T1 test 8 = Mark T2 test 20 = T1 test parameter settings 300 = European factory settings 301= Pakistani factory settings 0x2345=short read enable
0x03 | 2022 | Waveform channel 0 |  | 2 | R/W
0x03 | 2023 | Waveform channel 1 |  | 2 | R/W
0x03 | 2024 | Waveform channel 2 |  | 2 | R/W
0x03 | 2025 | Waveform channel 3 |  | 2 | R/W
0x03 | 2026 | Data0 | Battery voltage | 2 | R | 0.01 | V |  | INT16
0x03 | 2027 | Data 1 | Battery Current | 2 | R | 0.1 | A | Positive means discharging, negative means charging | INT16
0x03 | 2028 | Data 2 | Photovoltaic 1 voltage | 2 | R | 0.1 | V | Positive means discharge and is always positive | INT16
0x03 | 2029 | Data 3 | Photovoltaic 1 current | 2 | R | 0.01 | A |  | INT16
0x03 | 2030 | Data 4 | Photovoltaic 2 voltage | 2 | R | 0.1 | V |  | INT16
0x03 | 2031 | Data 5 | Photovoltaic 2 current | 2 | R | 0.01 | A |  | INT16
0x03 | 2032 | Data 6 | Bus voltage | 2 | R | 0.1 | V |  | INT16
0x03 | 2033 | Data 7 | Positive bus voltage | 2 | R | 0.1 | V |  | INT16
0x03 | 2034 | Data 8 | Buck voltage | 2 | R | 0.1 | V |  | INT16
0x03 | 2035 | Data 9 | Buck current | 2 | R | 0.01 | A |  | INT16
0x03 | 2036 | Data 10 | Battery power | 2 | R | 1 | W | Positive means discharging, negative means charging | INT16
0x03 | 2037 | Data 11 | Photovoltaic 1 power | 2 | R | 1 | W |  | INT16
0x03 | 2038 | Data 12 | Photovoltaic 2 power | 2 | R | 1 | W |  | INT16
0x03 | 2039 | Data 13 | Battery SOC | 2 | R | 1 | % |  | UINT16
0x03 | 2040 | Data 14 | Transformer current | 2 | R | 0.01 | A
0x03 | 2041 | Data 15 | Low voltage DC voltage | 2 | R | 0.01 | V
0x03 | 2042 | Data 16 |  | 2 | R
0x03 | 2043 | Data 17 | Substrate temperature 1 | 2 | R
0x03 | 2044 | Data 18 | Substrate temperature 2 | 2 | R
0x03 | 2045 | Data 19 | Substrate temperature 3 | 2 | R
0x03 | 2046 | Data 20 | Substrate temperature 4 | 2 | R
0x03 | 2047 | Data 21 | Radiator temperature 1 | 2 | R
0x03 | 2048 | Data 22 | Radiator temperature 2 | 2 | R
0x03 | 2049 | Data 23 | Radiator temperature 3 | 2 | R
0x03 | 2050 | Data 24 | Radiator temperature 4 | 2 | R
0x03 | 2051 | Data 25 | T1 test logo | 2 | R |  |  | 16=T1 test completed 17=T1&T2 completed
0x03 | 2052 | Data 26 | upgrade enable | 2 | R |  |  | bit12=1 upgrade enable bit13=1 short read enable bit7-bit0 boot version
0x03 | 2053 | Data 27 | PV1Working stage | 2 | R |  |  |  | UINT16
0x03 | 2054 | Data 28 | PV2 working stage | 2 | R |  |  |  | UINT16
0x03 | 2055 | Data 29 | Battery temperature | 2 | R | 0.1 | ℃ |  | UINT16
0x03 | 2056 | Data 30 | Maximum temperature | 2 | R | 0.1 | ℃ |  | UINT16
0x03 | 2057 | Data 31 | Battery working stage | 2 | R |  |  |  | UINT16
0x03 | 2058 | Data 32 | Machine operating status | 2 | R |  |  | Table 10 | UINT16
0x03 | 2059 | Data 33 | Leakage Current | 2 | R
0x03 | 2060 | Data 34 | Insulation resistance | 2 | R
0x03 | 2061 | Data 35 | Alarm status word 1 | 2 | R |  |  | See fault information table | UINT16
0x03 | 2062 | Data 36 | Alarm status word 2 | 2 | R |  |  |  | UINT16
0x03 | 2063 | Data 37 | Fault status word 1 | 2 | R |  |  |  | UINT16
0x03 | 2064 | Data 38 | Fault status word 2 | 2 | R |  |  |  | UINT16
0x03 | 2065 | Data 39 | Photovoltaic power generation on the day | 2 | R | 0.1 | kW |  | UINT16
0x03 | 2066 | Data 40 | Total photovoltaic power generation | 2 | R | 0.1 | kW | High 16-digit | UINT16
0x03 | 2067 | Data 41 |  | 2 | R |  | kW | Low 16-digit | UINT16
0x03 | 2068 | Data 42 | Battery charge level for the day | 2 | R | 0.1 | kW |  | UINT16
0x03 | 2069 | Data 43 | Total battery charge | 2 | R | 0.1 | kW | High 16-digit | UINT16
0x03 | 2070 | Data 44 |  | 2 | R |  | kW | Low 16-digit | UINT16
0x03 | 2071 | Data 45 | Battery discharge on the day | 2 | R | 0.1 | kW |  | UINT16
0x03 | 2072 | Data 46 | Total battery discharge | 2 | R | 0.1 | kW | High 16-digit | UINT16
0x03 | 2073 | Data 47 |  | 2 | R |  | kW | Low 16-digit | UINT16
0x03 | 2074 | Data 48 | The power grid purchased electricity on that day | 2 | R | 0.1 | kW |  | UINT16
0x03 | 2075 | Data 49 | Total power grid purchase electricity | 2 | R | 0.1 | kW | High 16-digit | UINT16
0x03 | 2076 | Data 50 |  | 2 | R |  | kW | Low 16-digit | UINT16
0x03 | 2077 | Data 51 | The power grid sold electricity on that day | 2 | R | 0.1 | kW |  | UINT16
0x03 | 2078 | Data 52 | Total power grid sold electricity | 2 | R | 0.1 | kW | High 16-digit | UINT16
0x03 | 2079 | Data 53 |  | 2 | R |  | kW | Low 16-digit | UINT16
0x03 | 2080 | Data 54 | Load power consumption on the day | 2 | R | 0.1 | kW |  | UINT16
0x03 | 2081 | Data 55 | Total load total power consumption | 2 | R | 0.1 | kW | High 16-digit | UINT16
0x03 | 2082 | Data 56 |  | 2 | R |  | kW | Low 16-digit | UINT16
0x03 | 2083 | Data 57 |  | 2 | R
0x03 | 2084 | Data 58 |  | 2 | R
0x03 | 2085 | Data 59 |  | 2 | R
0x03 | 2086 | Data 60 |  | 2 | R
0x03 | 2087 | Data 61 | DCDC software BOOT version (lower 8 bits) | 2 | R
0x03 | 2088 | Data 62 | DCDC software version low 8 digit minor version | 2 | R |  |  |  | UINT16
0x03 | 2089 | Data 63 | DCDC software version 16-bit large version | 2 | R |  |  |  | UINT16
0x03 | 2090 | Module online status |  | 2 | R |  |  |  | UINT16

## Parameter Group
Inverter unit parameter address
Order | Register Address | Parameter Group | Serial number | Data Type | Number of bytes | R/W | unit |  | Parameter Description | scope
0x03 | 640 | Group 0 | 0 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 0
0x03 | 641 |  | 1 | Parameter 1 | 2 | R/W |  |  | Communication address 1 | 0~63odd number | Com Addr
0x03 | 642 |  | 2 | Parameter 2 | 2 | R/W | 0.1 | V | Inverter rated voltage | 2180~2320 | INV Rated Voltage
0x03 | 643 |  | 3 | Parameter 3 | 2 | R/W | 0.01 | Hz | Inverter rated frequency | 4600~5400 | INV Rated Freq
0x03 | 644 |  | 4 | Parameter 4 | 2 | R/W | 0.01 | A | Maximum on-grid current | 0~2600 | Max INV Current
0x03 | 645 |  | 5 | Parameter 5 | 2 | R/W | 0.1 | V | Maximum grid voltage | 1980~2640
0x03 | 646 |  | 6 | Parameter 6 | 2 | R/W | 0.1 | V | Minimum grid voltage | 1980~2640
0x03 | 647 |  | 7 | Parameter 7 | 2 | R/W | 0.01 | Hz | Maximum grid frequency | 4600~5400 | The Range of V_grid
0x03 | 648 |  | 8 | Parameter 8 | 2 | R/W | 0.01 | Hz | Minimum grid frequency | 4600~5400
0x03 | 649 |  | 9 | Parameter 9 | 2 | R/W | 0.01 | Hz | Maximum frequency of generator | 4600~5400
0x03 | 650 |  | 10 | Parameter 10 | 2 | R/W | 0.01 | Hz | Minimum frequency of generator | 4600~5400
0x03 | 651 |  | 11 | Parameter 11 | 2 | R/W |  |  | Communication address 2 | 0~63odd number
0x03 | 652 |  | 12 | Parameter 12 | 2 | R/W | 0.1 | V | Maximum voltage of generator | 1980~2640
0x03 | 653 |  | 13 | Parameter 13 | 2 | R/W | 0.1 | V | Minimum voltage of generator | 1980~2640
0x03 | 654 | Group 1 | 14 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 1
0x03 | 655 |  | 15 | Parameter 1 | 2 | R/W |  |  | Set year data | 0~99
0x03 | 656 |  | 16 | Parameter 2 | 2 | R/W |  |  | Set monthly data | 1~12
0x03 | 657 |  | 17 | Parameter 3 | 2 | R/W |  |  | Set weekly data | 1~7
0x03 | 658 |  | 18 | Parameter 4 | 2 | R/W |  |  | Set daily data | 1~31
0x03 | 659 |  | 19 | Parameter 5 | 2 | R/W |  |  | Set the hours | 0~23
0x03 | 660 |  | 20 | Parameter 6 | 2 | R/W |  |  | Set the minutes | 0~59
0x03 | 661 |  | 21 | Parameter 7 | 2 | R/W |  |  | Set the seconds | 0~59
0x03 | 662 |  | 22 | Parameter 8 | 2 | R/W |  |  | Startup Settings | 16
0x03 | 663 |  | 23 | Parameter 9 | 2 | R/W
0x03 | 664 |  | 24 | Parameter 10 | 2 | R/W
0x03 | 665 |  | 25 | Parameter 11 | 2 | R/W |  |  | PEN relay enable | 85: enable
0x03 | 666 |  | 26 | Parameter 12 | 2 | R/W
0x03 | 667 |  | 27 | Parameter 13 | 2 | R/W
0x03 | 668 | Group 2 | 28 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 2
0x03 | 669 |  | 29 | Parameter 1 | 2 | R/W
0x03 | 670 |  | 30 | Parameter 2 | 2 | R/W |  |  | on-grid reconnect time | 60
0x03 | 671 |  | 31 | Parameter 3 | 2 | R/W
0x03 | 672 |  | 32 | Parameter 4 | 2 | R/W
0x03 | 673 |  | 33 | Parameter 5 | 2 | R/W
0x03 | 674 |  | 34 | Parameter 6 | 2 | R/W
0x03 | 675 |  | 35 | Parameter 7 | 2 | R/W
0x03 | 676 |  | 36 | Parameter 8 | 2 | R/W
0x03 | 677 |  | 37 | Parameter 9 | 2 | R/W |  |  |  | 3000
0x03 | 678 |  | 38 | Parameter 10 | 2 | R/W |  |  |  | 6000
0x03 | 679 |  | 39 | Parameter 11 | 2 | R/W |  |  |  | 3000
0x03 | 680 |  | 40 | Parameter 12 | 2 | R/W |  |  |  | 6000
0x03 | 681 |  | 41 | Parameter 13 | 2 | R/W
0x03 | 682 | Group 3 | 42 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 3
0x03 | 683 |  | 43 | Parameter 1 | 2 | R/W
0x03 | 684 |  | 44 | Parameter 2 | 2 | R/W
0x03 | 685 |  | 45 | Parameter 3 | 2 | R/W
0x03 | 686 |  | 46 | Parameter 4 | 2 | R/W
0x03 | 687 |  | 47 | Parameter 5 | 2 | R/W
0x03 | 688 |  | 48 | Parameter 6 | 2 | R/W
0x03 | 689 |  | 49 | Parameter 7 | 2 | R/W
0x03 | 690 |  | 50 | Parameter 8 | 2 | R/W
0x03 | 691 |  | 51 | Parameter 9 | 2 | R/W
0x03 | 692 |  | 52 | Parameter 10 | 2 | R/W
0x03 | 693 |  | 53 | Parameter 11 | 2 | R/W
0x03 | 694 |  | 54 | Parameter 12 | 2 | R/W
0x03 | 695 |  | 55 | Parameter 13 | 2 | R/W
0x03 | 696 | Group 4 | 56 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 4
0x03 | 697 |  | 57 | Parameter 1 | 2 | R/W | 1 |  | Bypass initialization settings
0x03 | 698 |  | 58 | Parameter 2 | 2 | R/W | 1 |  | Generator settings
0x03 | 699 |  | 59 | Parameter 3 | 2 | R/W | 1 |  | Automatic power-on enable | 5=Enable
0x03 | 700 |  | 60 | Parameter 4 | 2 | R/W | 1 | W | Maximum power selling | 0-12000
0x03 | 701 |  | 61 | Parameter 5 | 2 | R/W |  |  | Generator interface type | 5=smart 10=AC Couple Other=Diesel Generator
0x03 | 702 |  | 62 | Parameter 6 | 2 | R/W |  |  | Smart Mode(always on) | 0x05=Ongrid always On Enable 0x50=only bat on Enable
0x03 | 703 |  | 63 | Parameter 7 | 2 | R/W |  |  | Generator start signal enable | 0x05=GenStart Enable Other = Prohibited
0x03 | 704 |  | 64 | Parameter 8 | 2 | R/W | 0.01
0x03 | 705 |  | 65 | Parameter 9 | 2 | R/W |  |  | Diesel Generator mode | 5=Vf mode Other = PQ mode
0x03 | 706 |  | 66 | Parameter 10 | 2 | R/W |  |  | Number of parallel units | 0 = Single machine > 0 = Number of parallel machines 0-4
0x03 | 707 |  | 67 | Parameter 11 | 2 | R/W | 0.01 | Hz | AC couple frequency | 5000-6500
0x03 | 708 |  | 68 | Parameter 12 | 2 | R/W |  |  | External Current Hall Rating | 100
0x03 | 709 |  | 69 | Parameter 13 | 2 | R/W |  |  | Current Control Mode | 1=CT 5=electricity meter
0x03 | 710 | Group 5 | 70 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 5
0x03 | 711 |  | 71 | Parameter 1 | 2 | R/W
0x03 | 712 |  | 72 | Parameter 2 | 2 | R/W
0x03 | 713 |  | 73 | Parameter 3 | 2 | R/W
0x03 | 714 |  | 74 | Parameter 4 | 2 | R/W
0x03 | 715 |  | 75 | Parameter 5 | 2 | R/W
0x03 | 716 |  | 76 | Parameter 6 | 2 | R/W
0x03 | 717 |  | 77 | Parameter 7 | 2 | R/W
0x03 | 718 |  | 78 | Parameter 8 | 2 | R/W
0x03 | 719 |  | 79 | Parameter 9 | 2 | R/W
0x03 | 720 |  | 80 | Parameter 10 | 2 | R/W
0x03 | 721 |  | 81 | Parameter 11 | 2 | R/W
0x03 | 722 |  | 82 | Parameter 12 | 2 | R/W
0x03 | 723 |  | 83 | Parameter 13 | 2 | R/W
0x03 | 724 | Group 6 | 84 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 6
0x03 | 725 |  | 85 | Parameter 1 | 2 | R/W
0x03 | 726 |  | 86 | Parameter 2 | 2 | R/W
0x03 | 727 |  | 87 | Parameter 3 | 2 | R/W
0x03 | 728 |  | 88 | Parameter 4 | 2 | R/W
0x03 | 729 |  | 89 | Parameter 5 | 2 | R/W
0x03 | 730 |  | 90 | Parameter 6 | 2 | R/W
0x03 | 731 |  | 91 | Parameter 7 | 2 | R/W
0x03 | 732 |  | 92 | Parameter 8 | 2 | R/W
0x03 | 733 |  | 93 | Parameter 9 | 2 | R/W
0x03 | 734 |  | 94 | Parameter 10 | 2 | R/W
0x03 | 735 |  | 95 | Parameter 11 | 2 | R/W
0x03 | 736 |  | 96 | Parameter 12 | 2 | R/W
0x03 | 737 |  | 97 | Parameter 13 | 2 | R/W
0x03 | 738 | Group 7 | 98 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 7
0x03 | 739 |  | 99 | Parameter 1 | 2 | R/W
0x03 | 740 |  | 100 | Parameter 2 | 2 | R/W
0x03 | 741 |  | 101 | Parameter 3 | 2 | R/W
0x03 | 742 |  | 102 | Parameter 4 | 2 | R/W | 1 | 0.1℃ | Over temperature protection limit
0x03 | 743 |  | 103 | Parameter 5 | 2 | R/W
0x03 | 744 |  | 104 | Parameter 6 | 2 | R/W
0x03 | 745 |  | 105 | Parameter 7 | 2 | R/W
0x03 | 746 |  | 106 | Parameter 8 | 2 | R/W
0x03 | 747 |  | 107 | Parameter 9 | 2 | R/W
0x03 | 748 |  | 108 | Parameter 10 | 2 | R/W
0x03 | 749 |  | 109 | Parameter 11 | 2 | R/W
0x03 | 750 |  | 110 | Parameter 12 | 2 | R/W
0x03 | 751 |  | 111 | Parameter 13 | 2 | R/W
0x03 | 1504 | Group 8 | 0 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 8
0x03 | 1505 |  | 1 | Parameter 1 | 2 | R/W | 0.1 |  | Positive DC bus bias | '-100~100
0x03 | 1506 |  | 2 | Parameter 2 | 2 | R/W | 0.0001 |  | Positive DC bus slope | '-1000~1000
0x03 | 1507 |  | 3 | Parameter 3 | 2 | R/W | 0.1 |  | Negative DC bus bias | '-100~100
0x03 | 1508 |  | 4 | Parameter 4 | 2 | R/W | 0.0001 |  | Negative DC bus slope | '-1000~1000
0x03 | 1509 |  | 5 | Parameter 5 | 2 | R/W | 0.1 |  | Inverter voltage A slope | '-1000~1000
0x03 | 1510 |  | 6 | Parameter 6 | 2 | R/W | 0.0001 |  | Inverter voltage B slope | '-1000~1000
0x03 | 1511 |  | 7 | Parameter 7 | 2 | R/W | 0.1 |  | Inverter voltage C slope | '-1000~1000
0x03 | 1512 |  | 8 | Parameter 8 | 2 | R/W | 0.0001 |  | Output voltage A slope | '-1000~1000
0x03 | 1513 |  | 9 | Parameter 9 | 2 | R/W | 0.1 |  | Output voltage B slope | '-1000~1000
0x03 | 1514 |  | 10 | Parameter 10 | 2 | R/W | 0.0001 |  | Output voltage C slope | '-1000~1000
0x03 | 1515 |  | 11 | Parameter 11 | 2 | R/W | 0.1 |  | Grid = bypass voltage A slope | '-100~100
0x03 | 1516 |  | 12 | Parameter 12 | 2 | R/W | 0.0001 |  | Grid = bypass voltage B slope | '-1000~1000
0x03 | 1517 |  | 13 | Parameter 13 | 2 | R/W |  |  | Grid = bypass voltage C slope
0x03 | 1518 | Group 9 | 14 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 9
0x03 | 1519 |  | 15 | Parameter 1 | 2 | R/W | 0.1 |  | Diesel generator voltage A slope | '-100~100
0x03 | 1520 |  | 16 | Parameter 2 | 2 | R/W | 0.0001 |  | Diesel generator voltage B slope | '-1000~1000
0x03 | 1521 |  | 17 | Parameter 3 | 2 | R/W | 0.1 |  | Diesel generator voltage C slope | '-100~100
0x03 | 1522 |  | 18 | Parameter 4 | 2 | R/W | 0.0001 |  |  | '-1000~1000
0x03 | 1523 |  | 19 | Parameter 5 | 2 | R/W | 0.0001 |  | Phase A CT current slope | '-1000~1000
0x03 | 1524 |  | 20 | Parameter 6 | 2 | R/W | 0.0001 |  | Phase B CT current slope | '-1000~1000
0x03 | 1525 |  | 21 | Parameter 7 | 2 | R/W | 0.0001 |  | Phase C CT current slope | '-1000~1000
0x03 | 1526 |  | 22 | Parameter 8 | 2 | R/W | 0.0001 |  | A phase diesel generator current slope | '-1000~1000
0x03 | 1527 |  | 23 | Parameter 9 | 2 | R/W | 0.0001 |  | B phase diesel generator current slope | '-1000~1000
0x03 | 1528 |  | 24 | Parameter 10 | 2 | R/W | 0.0001 |  | C phase diesel generator current slope | '-1000~1000
0x03 | 1529 |  | 25 | Parameter 11 | 2 | R/W |  |  | reserve
0x03 | 1530 |  | 26 | Parameter 12 | 2 | R/W |  |  | reserve
0x03 | 1531 |  | 27 | Parameter 13 | 2 | R/W |  |  | reserve
0x03 | 1532 | Group 10 | 28 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 10
0x03 | 1533 |  | 29 | Parameter 1 | 2 | R/W | 0.0001 |  | Phase A inductor current slope | '-1000~1000
0x03 | 1534 |  | 30 | Parameter 2 | 2 | R/W | 0.0001 |  | Phase B inductor current slope | '-1000~1000
0x03 | 1535 |  | 31 | Parameter 3 | 2 | R/W | 0.0001 |  | Phase C inductor current slope | '-1000~1000
0x03 | 1536 |  | 32 | Parameter 4 | 2 | R/W | 0.0001 |  | A phase inverter current slope | '-1000~1000
0x03 | 1537 |  | 33 | Parameter 5 | 2 | R/W | 0.0001 |  | B phase inverter current slope | '-1000~1000
0x03 | 1538 |  | 34 | Parameter 6 | 2 | R/W | 0.0001 |  | C phase inverter current slope | '-1000~1000
0x03 | 1539 |  | 35 | Parameter 7 | 2 | R/W | 0.0001 |  | Phase A grid current slope | '-1000~1000
0x03 | 1540 |  | 36 | Parameter 8 | 2 | R/W | 0.0001 |  | Phase B grid current slope | '-1000~1000
0x03 | 1541 |  | 37 | Parameter 9 | 2 | R/W | 0.0001 |  | Phase C grid current slope | '-1000~1000
0x03 | 1542 |  | 38 | Parameter 10 | 2 | R/W | 0.0001 |  | Phase A load current slope | '-1000~1000
0x03 | 1543 |  | 39 | Parameter 11 | 2 | R/W | 0.0001 |  | Phase B load current slope | '-1000~1000
0x03 | 1544 |  | 40 | Parameter 12 | 2 | R/W | 0.0001 |  | Phase C load current slope | '-1000~1000
0x03 | 1545 |  | 41 | Parameter 13 | 2 | R/W |  |  | reserve
0x03 | 1546 | Group 11 | 42 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 11
0x03 | 1547 |  | 43 | Parameter 1 | 2 | R/W | 0.0001 |  | Safety Standards
0x03 | 1548 |  | 44 | Parameter 2 | 2 | R/W | 0.0001
0x03 | 1549 |  | 45 | Parameter 3 | 2 | R/W | 0.0001
0x03 | 1550 |  | 46 | Parameter 4 | 2 | R/W | 0.0001
0x03 | 1551 |  | 47 | Parameter 5 | 2 | R/W | 0.0001
0x03 | 1552 |  | 48 | Parameter 6 | 2 | R/W | 0.0001
0x03 | 1553 |  | 49 | Parameter 7 | 2 | R/W | 0.0001
0x03 | 1554 |  | 50 | Parameter 8 | 2 | R/W | 0.0001 |  |  | 8：Disconnection reconnects enable
0x03 | 1555 |  | 51 | Parameter 9 | 2 | R/W | 0.0001 |  | Meter parameter settings | bit0-bit3:Meter address bit4-bit7:Electric meter manufacturers 0-Eastron 1-CHINT
0x03 | 1556 |  | 52 | Parameter 10 | 2 | R/W | 0.0001
0x03 | 1557 |  | 53 | Parameter 11 | 2 | R/W | 0.0001
0x03 | 1558 |  | 54 | Parameter 12 | 2 | R/W | 0.0001
0x03 | 1559 |  | 55 | Parameter 13 | 2 | R/W
0x03 | 1560 | Group 12 | 56 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 12
0x03 | 1561 |  | 57 | Parameter 1 | 2 | R/W
0x03 | 1562 |  | 58 | Parameter 2 | 2 | R/W
0x03 | 1563 |  | 59 | Parameter 3 | 2 | R/W
0x03 | 1564 |  | 60 | Parameter 4 | 2 | R/W
0x03 | 1565 |  | 61 | Parameter 5 | 2 | R/W
0x03 | 1566 |  | 62 | Parameter 6 | 2 | R/W
0x03 | 1567 |  | 63 | Parameter 7 | 2 | R/W
0x03 | 1568 |  | 64 | Parameter 8 | 2 | R/W
0x03 | 1569 |  | 65 | Parameter 9 | 2 | R/W
0x03 | 1570 |  | 66 | Parameter 10 | 2 | R/W
0x03 | 1571 |  | 67 | Parameter 11 | 2 | R/W
0x03 | 1572 |  | 68 | Parameter 12 | 2 | R/W
0x03 | 1573 |  | 69 | Parameter 13 | 2 | R/W
0x03 | 1574 | Group 13 | 70 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 13
0x03 | 1575 |  | 71 | Parameter 1 | 2 | R/W
0x03 | 1576 |  | 72 | Parameter 2 | 2 | R/W
0x03 | 1577 |  | 73 | Parameter 3 | 2 | R/W
0x03 | 1578 |  | 74 | Parameter 4 | 2 | R/W
0x03 | 1579 |  | 75 | Parameter 5 | 2 | R/W
0x03 | 1580 |  | 76 | Parameter 6 | 2 | R/W
0x03 | 1581 |  | 77 | Parameter 7 | 2 | R/W
0x03 | 1582 |  | 78 | Parameter 8 | 2 | R/W
0x03 | 1583 |  | 79 | Parameter 9 | 2 | R/W
0x03 | 1584 |  | 80 | Parameter 10 | 2 | R/W
0x03 | 1585 |  | 81 | Parameter 11 | 2 | R/W
0x03 | 1586 |  | 82 | Parameter 12 | 2 | R/W
0x03 | 1587 |  | 83 | Parameter 13 | 2 | R/W
0x03 | 1588 | Group 14 | 84 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 14
0x03 | 1589 |  | 85 | Parameter 1 | 2 | R/W
0x03 | 1590 |  | 86 | Parameter 2 | 2 | R/W
0x03 | 1591 |  | 87 | Parameter 3 | 2 | R/W
0x03 | 1592 |  | 88 | Parameter 4 | 2 | R/W
0x03 | 1593 |  | 89 | Parameter 5 | 2 | R/W
0x03 | 1594 |  | 90 | Parameter 6 | 2 | R/W
0x03 | 1595 |  | 91 | Parameter 7 | 2 | R/W
0x03 | 1596 |  | 92 | Parameter 8 | 2 | R/W
0x03 | 1597 |  | 93 | Parameter 9 | 2 | R/W
0x03 | 1598 |  | 94 | Parameter 10 | 2 | R/W
0x03 | 1599 |  | 95 | Parameter 11 | 2 | R/W
0x03 | 1600 |  | 96 | Parameter 12 | 2 | R/W
0x03 | 1601 |  | 97 | Parameter 13 | 2 | R/W
0x03 | 1602 | Group 15 | 98 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 15
0x03 | 1603 |  | 99 | Parameter 1 | 2 | R/W
0x03 | 1604 |  | 100 | Parameter 2 | 2 | R/W
0x03 | 1605 |  | 101 | Parameter 3 | 2 | R/W
0x03 | 1606 |  | 102 | Parameter 4 | 2 | R/W
0x03 | 1607 |  | 103 | Parameter 5 | 2 | R/W
0x03 | 1608 |  | 104 | Parameter 6 | 2 | R/W
0x03 | 1609 |  | 105 | Parameter 7 | 2 | R/W
0x03 | 1610 |  | 106 | Parameter 8 | 2 | R/W
0x03 | 1611 |  | 107 | Parameter 9 | 2 | R/W
0x03 | 1612 |  | 108 | Parameter 10 | 2 | R/W
0x03 | 1613 |  | 109 | Parameter 11 | 2 | R/W |  |  | Parallel communication test | 5=Test Enable
0x03 | 1614 |  | 110 | Parameter 12 | 2 | R/W |  |  | Aging Mode | 4=Aging Mode
0x03 | 1615 |  | 111 | Parameter 13 | 2 | R/W |  |  | K12=156,K13=189Online Upgrade | 0
DC unit parameter address
Order | Register Address | Parameter Group | Serial number | Data Type | Number of bytes | R/W | unit |  | Parameter Description | scope
0x03 | 2640 | Group 0 | 0 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 0
0x03 | 2641 |  | 1 | Parameter 1 | 2 | R/W |  |  | communication address 1 | 0~63even number | Com Addr
0x03 | 2642 |  | 2 | Parameter 2 | 2 | R/W | 0.01 | V | Maximum battery voltage | 4800~6000 | Max V_charge Of BAT
0x03 | 2643 |  | 3 | Parameter 3 | 2 | R/W | 0.01 | V | Minimum battery voltage | 3500-~5500 | Min V_discharge Of BAT
0x03 | 2644 |  | 4 | Parameter 4 | 2 | R/W | 0.1 | A | Maximum battery charging current | 0~2500 | Battery Capacity
0x03 | 2645 |  | 5 | Parameter 5 | 2 | R/W | 0.1 | A | Maximum battery discharge current | 0~2500 | Max I_charge Of BAT
0x03 | 2646 |  | 6 | Parameter 6 | 2 | R/W | 1 | AH | Battery capacity | 10~2000 | Min I_discharge Of BAT
0x03 | 2647 |  | 7 | Parameter 7 | 2 | R/W | 0.1 | V | Photovoltaic 1 maximum voltage | 1600~8000 | Max Voltage Of PV1
0x03 | 2648 |  | 8 | Parameter 8 | 2 | R/W | 0.01 | A | Photovoltaic 1 maximum current | 0~2600 | Max Current Of PV1
0x03 | 2649 |  | 9 | Parameter 9 | 2 | R/W | 0.1 | V | Photovoltaic 2 maximum voltage | 1600~8000 | Max Voltage Of PV2
0x03 | 2650 |  | 10 | Parameter 10 | 2 | R/W | 0.01 | A | Photovoltaic 2 maximum current | 0~1700 | Max Current Of PV2
0x03 | 2651 |  | 11 | Parameter 11 | 2 | R/W |  |  | communication address 2 | 0~63even number
0x03 | 2652 |  | 12 | Parameter 12 | 2 | R/W |  |  | Battery Type | 0x5-Lithium battery;0x50-Non-lithium battery (voltage control)
0x03 | 2653 |  | 13 | Parameter 13 | 2 | R/W
0x03 | 2654 | Group 1 | 14 | Parameter 0 | 2 | R/W |  |  |  | 1
0x03 | 2655 |  | 15 | Parameter 1 | 2 | R/W | 1 | W | Maximum power of grid discharge | 0-12000
0x03 | 2656 |  | 16 | Parameter 2 | 2 | R/W | 1 | 1% | Grid discharge minimum SOC | 5-100
0x03 | 2657 |  | 17 | Parameter 3 | 2 | R/W | 1 | 1% | Maximum SOC for grid charging | 0-100
0x03 | 2658 |  | 18 | Parameter 4 | 2 | R/W | 0.01 | V | Grid discharge minimum voltage | 3700-6000
0x03 | 2659 |  | 19 | Parameter 5 | 2 | R/W | 0.01 | V | Maximum voltage for grid charging | 3700-6000
0x03 | 2660 |  | 20 | Parameter 6 | 2 | R/W | 0.1 | A | Maximum charging current of the power grid | 0-2500
0x03 | 2661 |  | 21 | Parameter 7 | 2 | R/W | 0.1 | A | Maximum diesel generator charging current | 0-2500
0x03 | 2662 |  | 22 | Parameter 8 | 2 | R/W | 1 | W | Maximum discharge power of diesel generator | 0-12000
0x03 | 2663 |  | 23 | Parameter 9 | 2 | R/W | 1 | 1% | Minimum SOC of diesel generator discharge | 10-100
0x03 | 2664 |  | 24 | Parameter 10 | 2 | R/W | 1 | 1% | Maximum SOC of diesel generator charging | 0-100
0x03 | 2665 |  | 25 | Parameter 11 | 2 | R/W | 0.01 | V | Minimum discharge voltage of diesel generator | 3700-6000
0x03 | 2666 |  | 26 | Parameter 12 | 2 | R/W | 0.01 | V | Maximum voltage for diesel generator charging | 3700-6000
0x03 | 2667 |  | 27 | Parameter 13 | 2 | R/W |  |  | The grid prohibits charging at the minimum SOC | 0-100
0x03 | 2668 | Group 2 | 28 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 2
0x03 | 2669 |  | 29 | Parameter 1 | 2 | R/W |  |  | Power control time1 | 0~2359
0x03 | 2670 |  | 30 | Parameter 2 | 2 | R/W |  |  | Power control time2 | 0~2359
0x03 | 2671 |  | 31 | Parameter 3 | 2 | R/W |  |  | Power control time3 | 0~2359
0x03 | 2672 |  | 32 | Parameter 4 | 2 | R/W |  |  | Power control time4 | 0~2359
0x03 | 2673 |  | 33 | Parameter 5 | 2 | R/W |  |  | Power control time5 | 0~2359
0x03 | 2674 |  | 34 | Parameter 6 | 2 | R/W |  |  | Power control time6 | 0~2359
0x03 | 2675 |  | 35 | Parameter 7 | 2 | R/W |  |  | Power control time7 | 0~2359
0x03 | 2676 |  | 36 | Parameter 8 | 2 | R/W |  |  | Power control time8 | 0~2359
0x03 | 2677 |  | 37 | Parameter 9 | 2 | R/W |  |  | Grid charging enable | 5=Enable | bit=1 enables
0x03 | 2678 |  | 38 | Parameter 10 | 2 | R/W |  |  | Generator charging enable | 5=Enable
0x03 | 2679 |  | 39 | Parameter 11 | 2 | R/W
0x03 | 2680 |  | 40 | Parameter 12 | 2 | R/W
0x03 | 2681 |  | 41 | Parameter 13 | 2 | R/W
0x03 | 2682 | Group 3 | 42 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 3
0x03 | 2683 |  | 43 | Parameter 1 | 2 | R/W | 1 | W | 0Point to control time1 Power | 0~+12000
0x03 | 2684 |  | 44 | Parameter 2 | 2 | R/W | 1 | W | Control time1To control time2Power | 0~+12000
0x03 | 2685 |  | 45 | Parameter 3 | 2 | R/W | 1 | W | Control time2To control time3Power | 0~+12000
0x03 | 2686 |  | 46 | Parameter 4 | 2 | R/W | 1 | W | Control time3To control time4Power | 0~+12000
0x03 | 2687 |  | 47 | Parameter 5 | 2 | R/W | 1 | W | Control time4To control time5Power | 0~+12000
0x03 | 2688 |  | 48 | Parameter 6 | 2 | R/W | 1 | W | Control time5To control time6Power | 0~+12000
0x03 | 2689 |  | 49 | Parameter 7 | 2 | R/W | 1 | W | Control time6To control time7Power | 0~+12000
0x03 | 2690 |  | 50 | Parameter 8 | 2 | R/W | 1 | W | Control time7To control time8Power | 0~+12000
0x03 | 2691 |  | 51 | Parameter 9 | 2 | R/W | 1 | W | Control time8arrivetwenty three:59Power | 0~+12000
0x03 | 2692 |  | 52 | Parameter 10 | 2 | R/W
0x03 | 2693 |  | 53 | Parameter 11 | 2 | R/W
0x03 | 2694 |  | 54 | Parameter 12 | 2 | R/W
0x03 | 2695 |  | 55 | Parameter 13 | 2 | R/W
0x03 | 2696 | Group 4 | 56 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 4
0x03 | 2697 |  | 57 | Parameter 1 | 2 | R/W | 1% |  | 0Point to control time1ofSOC | 0-100
0x03 | 2698 |  | 58 | Parameter 2 | 2 | R/W | 1% |  | Control time1To control time2SOC | 0-100
0x03 | 2699 |  | 59 | Parameter 3 | 2 | R/W | 1% |  | Control time2To control time3SOC | 0-100
0x03 | 2700 |  | 60 | Parameter 4 | 2 | R/W | 1% |  | Control time3To control time4SOC | 0-100
0x03 | 2701 |  | 61 | Parameter 5 | 2 | R/W | 1% |  | Control time4To control time5SOC | 0-100
0x03 | 2702 |  | 62 | Parameter 6 | 2 | R/W | 1% |  | Control time5To control time6SOC | 0-100
0x03 | 2703 |  | 63 | Parameter 7 | 2 | R/W | 1% |  | Control time6To control time7SOC | 0-100
0x03 | 2704 |  | 64 | Parameter 8 | 2 | R/W | 1% |  | Control time7To control time8SOC | 0-100
0x03 | 2705 |  | 65 | Parameter 9 | 2 | R/W | 1% |  | Control time8arrivetwenty three:59SOC | 0-100
0x03 | 2706 |  | 66 | Parameter 10 | 2 | R/W
0x03 | 2707 |  | 67 | Parameter 11 | 2 | R/W
0x03 | 2708 |  | 68 | Parameter 12 | 2 | R/W
0x03 | 2709 |  | 69 | Parameter 13 | 2 | R/W
0x03 | 2710 | Group 5 | 70 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 5
0x03 | 2711 |  | 71 | Parameter 1 | 2 | R/W | 0.01 | V | 0Point to control time1Voltage | 3700-6000
0x03 | 2712 |  | 72 | Parameter 2 | 2 | R/W | 0.01 | V | Control time1To control time2Voltage | 3700-6000
0x03 | 2713 |  | 73 | Parameter 3 | 2 | R/W | 0.01 | V | Voltage from control time 2 to control time 3 | 3700-6000
0x03 | 2714 |  | 74 | Parameter 4 | 2 | R/W | 0.01 | V | Voltage from control time 3 to control time 4 | 3700-6000
0x03 | 2715 |  | 75 | Parameter 5 | 2 | R/W | 0.01 | V | Voltage from control time 4 to control time 5 | 3700-6000
0x03 | 2716 |  | 76 | Parameter 6 | 2 | R/W | 0.01 | V | Voltage from control time 5 to control time 6 | 3700-6000
0x03 | 2717 |  | 77 | Parameter 7 | 2 | R/W | 0.01 | V | Voltage from control time 6 to control time 7 | 3700-6000
0x03 | 2718 |  | 78 | Parameter 8 | 2 | R/W | 0.01 | V | Voltage from control time 7 to control time 8 | 3700-6000
0x03 | 2719 |  | 79 | Parameter 9 | 2 | R/W | 0.01 | V | Control the voltage from 8 to 23:59 | 3700-6000
0x03 | 2720 |  | 80 | Parameter 10 | 2 | R/W
0x03 | 2721 |  | 81 | Parameter 11 | 2 | R/W
0x03 | 2722 |  | 82 | Parameter 12 | 2 | R/W
0x03 | 2723 |  | 83 | Parameter 13 | 2 | R/W
0x03 | 2724 | Group 6 | 84 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 6
0x03 | 2725 |  | 85 | Parameter 1 | 2 | R/W |  |  | Photovoltaic power sales to the grid | 5-Enable
0x03 | 2726 |  | 86 | Parameter 2 | 2 | R/W |  |  | Battery power sales to the grid | 5-Enable
0x03 | 2727 |  | 87 | Parameter 3 | 2 | R/W |  |  | Battery automatic activation enable | 0x50 Enable
0x03 | 2728 |  | 88 | Parameter 4 | 2 | R/W
0x03 | 2729 |  | 89 | Parameter 5 | 2 | R/W
0x03 | 2730 |  | 90 | Parameter 6 | 2 | R/W |  |  | Temperature correction enable | 5-Enable
0x03 | 2731 |  | 91 | Parameter 7 | 2 | R/W |  |  |  |  | Share
0x03 | 2732 |  | 92 | Parameter 8 | 2 | R/W |  |  | Generator control word | 0x5-generator charging enable 0x50-BatFirseEn
0x03 | 2733 |  | 93 | Parameter 9 | 2 | R/W |  |  | Grid control word | 0x5-grid charging enable; 0x50-Power Limit 0x100-Peak shaving enable
0x03 | 2734 |  | 94 | Parameter 10 | 2 | R/W |  |  | Time curve enable | 5
0x03 | 2735 |  | 95 | Parameter 11 | 2 | R/W | 0.1 | KW | Maximum power of the grid | 0-120
0x03 | 2736 |  | 96 | Parameter 12 | 2 | R/W | 0.1 | KW | Maximum power of generator | 0-120
0x03 | 2737 |  | 97 | Parameter 13 | 2 | R/W | 1 | W | Maximum reverse flow power | 0-200
0x03 | 2738 | Group 7 | 98 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 7
0x03 | 2739 |  | 99 | Parameter 1 | 2 | R/W
0x03 | 2740 |  | 100 | Parameter 2 | 2 | R/W
0x03 | 2741 |  | 101 | Parameter 3 | 2 | R/W
0x03 | 2742 |  | 102 | Parameter 4 | 2 | R/W
0x03 | 2743 |  | 103 | Parameter 5 | 2 | R/W
0x03 | 2744 |  | 104 | Parameter 6 | 2 | R/W
0x03 | 2745 |  | 105 | Parameter 7 | 2 | R/W
0x03 | 2746 |  | 106 | Parameter 8 | 2 | R/W
0x03 | 2747 |  | 107 | Parameter 9 | 2 | R/W
0x03 | 2748 |  | 108 | Parameter 10 | 2 | R/W
0x03 | 2749 |  | 109 | Parameter 11 | 2 | R/W
0x03 | 2750 |  | 110 | Parameter 12 | 2 | R/W |  |  | Photovoltaic on-grid factory test mode | 80=Photovoltaic power stability test mode
0x03 | 2751 |  | 111 | Parameter 13 | 2 | R/W
0x03 | 3504 | Group 8 | 0 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 8
0x03 | 3505 |  | 1 | Parameter 1 | 2 | R/W | 0.1 |  | Positive DC bus bias | '-100~100
0x03 | 3506 |  | 2 | Parameter 2 | 2 | R/W | 0.0001 |  | Positive DC bus slope | '-1000~1000
0x03 | 3507 |  | 3 | Parameter 3 | 2 | R/W | 0.1 |  | Negative DC bus bias | '-100~100
0x03 | 3508 |  | 4 | Parameter 4 | 2 | R/W | 0.0001 |  | Negative DC bus slope | '-1000~1000
0x03 | 3509 |  | 5 | Parameter 5 | 2 | R/W | 0.1 |  | Battery voltage bias | '-100~100
0x03 | 3510 |  | 6 | Parameter 6 | 2 | R/W | 0.0001 |  | Battery voltage slope | '-1000~1000
0x03 | 3511 |  | 7 | Parameter 7 | 2 | R/W | 0.1 |  | Photovoltaic 1 voltage bias | '-100~100
0x03 | 3512 |  | 8 | Parameter 8 | 2 | R/W | 0.0001 |  | PV 1 voltage slope | '-1000~1000
0x03 | 3513 |  | 9 | Parameter 9 | 2 | R/W | 0.1 |  | Photovoltaic 1 voltage bias | '-100~100
0x03 | 3514 |  | 10 | Parameter 10 | 2 | R/W | 0.0001 |  | PV 1 voltage slope | '-1000~1000
0x03 | 3515 |  | 11 | Parameter 11 | 2 | R/W | 0.1 |  | Low voltage DC bias | '-100~100
0x03 | 3516 |  | 12 | Parameter 12 | 2 | R/W | 0.0001 |  | Low voltage DC voltage slope | '-1000~1000
0x03 | 3517 |  | 13 | Parameter 13 | 2 | R/W |  |  | reserve
0x03 | 3518 | Group 9 | 14 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 9
0x03 | 3519 |  | 15 | Parameter 1 | 2 | R/W | 0.1 |  | Buck DC voltage bias | '-100~100
0x03 | 3520 |  | 16 | Parameter 2 | 2 | R/W | 0.0001 |  | Buck DC voltage slope | '-1000~1000
0x03 | 3521 |  | 17 | Parameter 3 | 2 | R/W
0x03 | 3522 |  | 18 | Parameter 4 | 2 | R/W
0x03 | 3523 |  | 19 | Parameter 5 | 2 | R/W
0x03 | 3524 |  | 20 | Parameter 6 | 2 | R/W
0x03 | 3525 |  | 21 | Parameter 7 | 2 | R/W
0x03 | 3526 |  | 22 | Parameter 8 | 2 | R/W
0x03 | 3527 |  | 23 | Parameter 9 | 2 | R/W
0x03 | 3528 |  | 24 | Parameter 10 | 2 | R/W
0x03 | 3529 |  | 25 | Parameter 11 | 2 | R/W |  |  | reserve
0x03 | 3530 |  | 26 | Parameter 12 | 2 | R/W |  |  | reserve
0x03 | 3531 |  | 27 | Parameter 13 | 2 | R/W |  |  | Battery boost switching frequency setting
0x03 | 3532 | Group 10 | 28 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 10
0x03 | 3533 |  | 29 | Parameter 1 | 2 | R/W | 0.1 |  | Battery Current Bias | '-1000~1000
0x03 | 3534 |  | 30 | Parameter 2 | 2 | R/W | 0.0001 |  | Battery current slope | '-1000~1000
0x03 | 3535 |  | 31 | Parameter 3 | 2 | R/W | 0.1 |  | Photovoltaic 1 current bias | '-1000~1000
0x03 | 3536 |  | 32 | Parameter 4 | 2 | R/W | 0.0001 |  | Photovoltaic 1 current slope | '-1000~1000
0x03 | 3537 |  | 33 | Parameter 5 | 2 | R/W | 0.1 |  | Photovoltaic 2 current bias | '-1000~1000
0x03 | 3538 |  | 34 | Parameter 6 | 2 | R/W | 0.0001 |  | Photovoltaic 2 current slope | '-1000~1000
0x03 | 3539 |  | 35 | Parameter 7 | 2 | R/W
0x03 | 3540 |  | 36 | Parameter 8 | 2 | R/W
0x03 | 3541 |  | 37 | Parameter 9 | 2 | R/W
0x03 | 3542 |  | 38 | Parameter 10 | 2 | R/W
0x03 | 3543 |  | 39 | Parameter 11 | 2 | R/W
0x03 | 3544 |  | 40 | Parameter 12 | 2 | R/W
0x03 | 3545 |  | 41 | Parameter 13 | 2 | R/W |  |  | reserve
0x03 | 3546 | Group 11 | 42 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 11
0x03 | 3547 |  | 43 | Parameter 1 | 2 | R/W | 1% |  | Smart Start SOC | '40~100
0x03 | 3548 |  | 44 | Parameter 2 | 2 | R/W | 1% |  | Smart Shutdown SOC | '30~95
0x03 | 3549 |  | 45 | Parameter 3 | 2 | R/W | 0.01V |  | Smart starting voltage | 4900~6000
0x03 | 3550 |  | 46 | Parameter 4 | 2 | R/W | 0.01V |  | Smart shutdown voltage | 4800~5800
0x03 | 3551 |  | 47 | Parameter 5 | 2 | R/W | 1W |  | Smart photovoltaic start power | 100~12000
0x03 | 3552 |  | 48 | Parameter 6 | 2 | R/W
0x03 | 3553 |  | 49 | Parameter 7 | 2 | R/W | 1% |  | Photovoltaic start-up SOC | 0~80
0x03 | 3554 |  | 50 | Parameter 8 | 2 | R/W | 1% |  | Photovoltaic shutdown SOC | 10~90
0x03 | 3555 |  | 51 | Parameter 9 | 2 | R/W | 0.1 |  | Bus maximum voltage | 0~4500
0x03 | 3556 |  | 52 | Parameter 10 | 2 | R/W | 0.1 |  | Bus minimum voltage | 0~3700
0x03 | 3557 |  | 53 | Parameter 11 | 2 | R/W | 0.01V |  | Photovoltaic starting voltage | 4000~5600
0x03 | 3558 |  | 54 | Parameter 12 | 2 | R/W | 0.01V |  | Photovoltaic shutdown voltage | 4200~5800
0x03 | 3559 |  | 55 | Parameter 13 | 2 | R/W | 0.1 | ℃ | Fan start temperature | 0`600
0x03 | 3560 | Group 12 | 56 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 12
0x03 | 3561 |  | 57 | Parameter 1 | 2 | R/W | 0.01 | V | Float charge voltage | 4600-6000 | Lead-acid batteries | bit15 | 3: Shared enable
0x03 | 3562 |  | 58 | Parameter 2 | 2 | R/W | 0.01 | V | Equalizing charging voltage | 4600-6000 |  | bit14
0x03 | 3563 |  | 59 | Parameter 3 | 2 | R/W |  |  | Float charge voltage temperature compensation coefficient | 1=0.1mV/℃ |  | bit13
0x03 | 3564 |  | 60 | Parameter 4 | 2 | R/W |  |  | Equalizing charging voltage temperature compensation coefficient | 1=0.1mV/℃ |  | bit12
0x03 | 3565 |  | 61 | Parameter 5 | 2 | R/W | 0.1 | mΩ | Battery internal resistance | 1=0.1mΩ |  | bit11 | 5: RS485 0: CAN
0x03 | 3566 |  | 62 | Parameter 6 | 2 | R/W | 1 | V | Shutdown voltage | 40-60 |  | bit10
0x03 | 3567 |  | 63 | Parameter 7 | 2 | R/W | 1 | V | Low voltage alarm voltage | 40-60 |  | bit9
0x03 | 3568 |  | 64 | Parameter 8 | 2 | R/W | 1 | V | Restart voltage | 40-60 |  | bit8
0x03 | 3569 |  | 65 | Parameter 9 | 2 | R/W |  |  | equalization hours |  |  | bit7
0x03 | 3570 |  | 66 | Parameter 10 | 2 | R/W |  |  | BMS protocal Number |  | Lithium battery | bit6
0x03 | 3571 |  | 67 | Parameter 11 | 2 | R/W | 1% |  | ShutdownSOC | 5-100 |  | bit5
0x03 | 3572 |  | 68 | Parameter 12 | 2 | R/W | 1% |  | Low battery alarm SOC | 5-100 |  | bit4
0x03 | 3573 |  | 69 | Parameter 13 | 2 | R/W | 1% |  | Restart SoC | 5-100 |  | bit3
0x03 | 3574 | Group 13 | 70 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 13 |  | bit2
0x03 | 3575 |  | 71 | Parameter 1 | 2 | R/W | [5 empty] | bit1
0x03 | 3576 |  | 72 | Parameter 2 | 2 | R/W | [5 empty] | bit0
0x03 | 3577 |  | 73 | Parameter 3 | 2 | R/W
0x03 | 3578 |  | 74 | Parameter 4 | 2 | R/W
0x03 | 3579 |  | 75 | Parameter 5 | 2 | R/W
0x03 | 3580 |  | 76 | Parameter 6 | 2 | R/W
0x03 | 3581 |  | 77 | Parameter 7 | 2 | R/W
0x03 | 3582 |  | 78 | Parameter 8 | 2 | R/W
0x03 | 3583 |  | 79 | Parameter 9 | 2 | R/W
0x03 | 3584 |  | 80 | Parameter 10 | 2 | R/W
0x03 | 3585 |  | 81 | Parameter 11 | 2 | R/W
0x03 | 3586 |  | 82 | Parameter 12 | 2 | R/W
0x03 | 3587 |  | 83 | Parameter 13 | 2 | R/W
0x03 | 3588 | Group 14 | 84 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 14
0x03 | 3589 |  | 85 | Parameter 1 | 2 | R/W
0x03 | 3590 |  | 86 | Parameter 2 | 2 | R/W
0x03 | 3591 |  | 87 | Parameter 3 | 2 | R/W
0x03 | 3592 |  | 88 | Parameter 4 | 2 | R/W
0x03 | 3593 |  | 89 | Parameter 5 | 2 | R/W
0x03 | 3594 |  | 90 | Parameter 6 | 2 | R/W
0x03 | 3595 |  | 91 | Parameter 7 | 2 | R/W
0x03 | 3596 |  | 92 | Parameter 8 | 2 | R/W
0x03 | 3597 |  | 93 | Parameter 9 | 2 | R/W
0x03 | 3598 |  | 94 | Parameter 10 | 2 | R/W
0x03 | 3599 |  | 95 | Parameter 11 | 2 | R/W
0x03 | 3600 |  | 96 | Parameter 12 | 2 | R/W
0x03 | 3601 |  | 97 | Parameter 13 | 2 | R/W
0x03 | 3602 | Group 15 | 98 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 31
0x03 | 3603 |  | 99 | Parameter 1 | 2 | R/W |  |  | BMS maximum charging current | 0-3000
0x03 | 3604 |  | 100 | Parameter 2 | 2 | R/W |  |  | BMS maximum discharge current | 0-3000
0x03 | 3605 |  | 101 | Parameter 3 | 2 | R/W | 0.01 | V | BMS charging maximum voltage | 4600-6000
0x03 | 3606 |  | 102 | Parameter 4 | 2 | R/W | 0.01 | V | BMS minimum discharge voltage | 4000-5400
0x03 | 3607 |  | 103 | Parameter 5 | 2 | R/W | 1% |  | BMS SOC | 0-100
0x03 | 3608 |  | 104 | Parameter 6 | 2 | R/W |  |  | BMS Status
0x03 | 3609 |  | 105 | Parameter 7 | 2 | R/W | 0.01 | V | BMSBattery voltage
0x03 | 3610 |  | 106 | Parameter 8 | 2 | R/W | 0.1 | A | BMSBattery Current
0x03 | 3611 |  | 107 | Parameter 9 | 2 | R/W
0x03 | 3612 |  | 108 | Parameter 10 | 2 | R/W
0x03 | 3613 |  | 109 | Parameter 11 | 2 | R/W
0x03 | 3614 |  | 110 | Parameter 12 | 2 | R/W |  |  |  | 0
0x03 | 3615 |  | 111 | Parameter 13 | 2 | R/W |  |  | K12=156,K13=189Online Upgrade | 0

## Historical fault records (hidden)
History
| Order | Register Address | Data Type | What the data means | Read and Write | byte | Unit ratio | Remark
|  | 1198 | short | History Page | Read and Write
| 0x03 | 1199 | short | Total number of records | Read and Write | 2 |  | 0-200
Record 1 | 0x03 | 1200 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1201 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1202 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1203 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 2 | 0x03 | 1204 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1205 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1206 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1207 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 3 | 0x03 | 1208 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1209 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1210 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1211 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 4 | 0x03 | 1212 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1213 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1214 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1215 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 5 | 0x03 | 1216 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1217 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1218 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1219 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 6 | 0x03 | 1220 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1221 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1222 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1223 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 7 | 0x03 | 1224 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1225 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1226 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1227 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 3 and the low byte is the record code
Record 8 | 0x03 | 1228 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1229 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1230 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1231 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 3 and the low byte is the record code
Record 9 | 0x03 | 1232 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1233 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1234 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1235 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 4 and the low byte is the record code
Record 10 | 0x03 | 1236 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1237 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1238 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1239 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
|  | 1348 | short | Event Log Page | Read and Write
|  | 1349 | short | Total number of event records | Read and Write
Event Log 1 | 0x03 | 1350 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1351 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1352 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1353 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 2 | 0x03 | 1354 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1355 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1356 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1357 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 3 | 0x03 | 1358 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1359 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1360 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1361 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 4 | 0x03 | 1362 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1363 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1364 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1365 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 5 | 0x03 | 1366 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1367 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1368 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1369 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 6 | 0x03 | 1370 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1371 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1372 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1373 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 7 | 0x03 | 1374 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1375 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1376 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1377 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 8 | 0x03 | 1378 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1379 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1380 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1381 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 9 | 0x03 | 1382 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1383 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1384 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1385 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 10 | 0x03 | 1386 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1387 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1388 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1389 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0

## Parameter settings
Serial number | Parameter name |  | illustrate/scope | unit |  | Data Types | Current Value | Setting Value
| English | Chinese |  |  |  |  | Register Address | parameter | Register Address | Setup Instructions | Reference interface
1 | [5 empty] | UINT16 |  | K0=1 | 5000 | When the setting parameter is delivered, K0 is fixed to 1, and K1-K10 should be within the calibration range of column D, for example, to set the maximum battery voltage to 58.5V, then K1=5850; To set the battery type to Use Bat V, K10=80 (0x50). To set the maximum battery discharge current Is -225.5A, then K4=-2255
2 | Bat V Max | Maximum battery voltage | 1500~6000 | 0.01 | V | UINT16 | 2642 | K1 | 5001
3 | Bat V Min | Minimum battery voltage | 1000~5500 | 0.01 | V | UINT16 | 2643 | K2 | 5002
4 | Max A Charge | Maximum battery charging current | 0~3000 | 0.1 | A | UINT16 | 2644 | K3 | 5003
5 | Max A DisCha | Maximum battery discharge current | -3000~0 | 0.1 | A | INT16 | 2645 | K4 | 5004
6 | Bat Cap AH | Battery capacity | 10~2000 | 1 | AH | UINT16 | 2646 | K5 | 5005
7 | PV1 V Max | Photovoltaic1Maximum voltage | 1600~8000 | 0.1 | V | UINT16 | 2647 | K6 | 5006
8 | PV1 A Max | Photovoltaic1Maximum current | 0~2600 | 0.01 | A | UINT16 | 2648 | K7 | 5007
9 | PV2 V Max | Photovoltaic2Maximum voltage | 1600~8000 | 0.1 | V | UINT16 | 2649 | K8 | 5008
10 | PV2 A Max | Photovoltaic2Maximum current | 0~1700 | 0.01 | A | UINT16 | 2650 | K9 | 5009
11 | Bat Mode | Battery Type | 0x0005 Lithium 0x0000 Use Bat V 0x0050 Use Bat % |  |  | UINT16 | 2652 | K10 | 5010
1 | [5 empty] | UINT16 |  | K0=2 | 5000 | When the setting parameter is delivered, K0 is fixed to 2, and K1-K15 should be within the calibration range of column D. For example, if the floating charging voltage is set to 58.5V, then K1=5850; To set the temperature correction enable (check), K10=5
2 | Float V | Float charge voltage | 4200~6000 | 0.01 | V | UINT16 | 3561 | K1 | 5001
3 | Equ V | Equalizing charging voltage | 4300~6000 | 0.01 | V | UINT16 | 3562 | K2 | 5002
4 | TempCoF | Float charge temperature compensation coefficient, | -100~0 | 0.1 | mV/℃ | INT16 | 3563 | K3 | 5003
5 | TempCoE | Equalizing charge temperature compensation coefficient | -100~0 | 0.1 | mV/℃ | INT16 | 3564 | K4 | 5004
6 | BatRes | Battery internal resistance | 0~1000 | 0.1 | mΩ | UINT16 | 3565 | K5 | 5005
7 | Shutdown | Inverter shutdown battery voltage | 4000-5400 | 0.01 | V | UINT16 | 3566 | K6 | 5006
8 | Low Bat | Inverter warning battery voltage | 4100-5500 | 0.01 | V | UINT16 | 3567 | K7 | 5007
9 | Restart | Inverter restart battery voltage | 4200-5600 | 0.01 | V | UINT16 | 3568 | K8 | 5008
10 | Equ Hours | Equalizing charge duration | 0-12000 | 1 | h | UINT16 | 3569 | K9 | 5009
11 | TempCoEn | Temperature correction enable | 5-Enable 0-prohibit |  |  | UINT16 | 2730 | K10 | 5010
12 | LiBatMode | Lithium battery mode | Display Hexadecimal |  |  | UINT16 | 3570 | K11 | 5011
13 | Shutdown | Inverter shutdown batterySOCvalue | 0-80 | 1 | % | UINT16 | 3571 | K12 | 5012
14 | Low Bat | Inverter alarm batterySOCvalue | 5-90 | 1 | % | UINT16 | 3572 | K13 | 5013
15 | Restart | Inverter restart batterySOCvalue | 10-100 | 1 | % | UINT16 | 3573 | K14 | 5014
16 | Equ Days | Equalizing charging interval time | 10-100 | 1 | day | UINT16 | 10007 | K15 | 5015
1 | [5 empty] | UINT16 |  | K0=3 | 5000 | When the setting parameter is delivered, K0 is fixed to 3, and K1-K13 must be within the calibration range of column D. For example, to set the maximum power of the grid discharge 12000W, K1=12000;
2 | Dischg Pmax W | Maximum power of grid discharge | 0~14000 | 1 | W | UINT16 | 2655 | K1 | 5001
3 | Dischg SOCmin -% | Minimum grid dischargeSOC | 5-100 | 1 | % | UINT16 | 2656 | K2 | 5002
4 | Chg SOCmax -% | Grid charging maximumSOC | 0-100 | 1 | % | UINT16 | 2657 | K3 | 5003
5 | Dischg Vmin -V | Grid discharge minimum voltage | 3700-6000 | 0.01 | V | UINT16 | 2658 | K4 | 5004
6 | Chg Vmax -V | Maximum voltage for grid charging | 3700-6000 | 0.01 | V | UINT16 | 2659 | K5 | 5005
7 | Chg Imax -A | Maximum charging current of the power grid | 0-2600 | 0.1 | A | UINT16 | 2660 | K6 | 5006
8 | Chg Imax -A | Maximum generator charging current | 0-2600 | 0.1 | A | UINT16 | 2661 | K7 | 5007
9 | Dischg Pmax W | Maximum discharge power of generator | 0~14000 | 1 | W | UINT16 | 2662 | K8 | 5008
10 | Dischg SOCmin -% | Minimum generator dischargeSOC | 10-100 | 1 | % | UINT16 | 2663 | K9 | 5009
11 | Chg SOCmax -% | Maximum generator chargingSOC | 0-100 | 1 | % | UINT16 | 2664 | K10 | 5010
12 | Dischg Vmin -V | Minimum discharge voltage of generator | 3700-6000 | 0.01 | V | UINT16 | 2665 | K11 | 5011
13 | Chg Vmax -V | Maximum voltage for generator charging | 3700-6000 | 0.01 | V | UINT16 | 2666 | K12 | 5012
14 | Disable Chg SOCmin-% | The grid prohibits charging at the minimumSOC | 0-100 | 1 | % | UINT16 | 2667 | K13 | 5013
1 | [5 empty] | UINT16 |  | K0=4 | 5000 | Time curve SOC page setup: When the setting parameter is delivered, K0 is fixed to 4, and K1-K20 should be within the calibration range of column D. For example, if the power control time 1 is set to 4:00, K1=0400; To set time curve enable (check box), K18=5
2 | 4:00 | Power control time1 | 0~2359 |  |  | UINT16 | 2669 | K1 | 5001
3 | 6:00 | Power control time2 | 0~2359 |  |  | UINT16 | 2670 | K2 | 5002
4 | 10:00 | Power control time3 | 0~2359 |  |  | UINT16 | 2671 | K3 | 5003
5 | 11:00 | Power control time4 | 0~2359 |  |  | UINT16 | 2672 | K4 | 5004
6 | 14:00 | Power control time5 | 0~2359 |  |  | UINT16 | 2673 | K5 | 5005
7 | 16:00 | Power control time6 | 0~2359 |  |  | UINT16 | 2674 | K6 | 5006
8 | 20:00 | Power control time7 | 0~2359 |  |  | UINT16 | 2675 | K7 | 5007
9 | 22:00 | Power control time8 | 0~2359 |  |  | UINT16 | 2676 | K8 | 5008
10 | 50 | 0Point to control time1ofSOC | 0-100 | 1 | % | UINT16 | 2697 | K9 | 5009
11 | 50 | Control time1To control time2ofSOC | 0-100 | 1 | % | UINT16 | 2698 | K10 | 5010
12 | 50 | Control time2To control time3ofSOC | 0-100 | 1 | % | UINT16 | 2699 | K11 | 5011
13 | 50 | Control time3To control time4ofSOC | 0-100 | 1 | % | UINT16 | 2700 | K12 | 5012
14 | 50 | Control time4To control time5ofSOC | 0-100 | 1 | % | UINT16 | 2701 | K13 | 5013
15 | 50 | Control time5To control time6ofSOC | 0-100 | 1 | % | UINT16 | 2702 | K14 | 5014
16 | 50 | Control time6To control time7ofSOC | 0-100 | 1 | % | UINT16 | 2703 | K15 | 5015
17 | 50 | Control time7To control time8ofSOC | 0-100 | 1 | % | UINT16 | 2704 | K16 | 5016
18 | 50 | Control time8arrivetwenty three:59ofSOC | 0-100 | 1 | % | UINT16 | 2705 | K17 | 5017
19 | Time of Use | Time curve enable | 5=Enable,0=Disable |  |  | UINT16 | 2734 | K18 | 5018
20 | GridChg | Grid charging enablement | bit=1Enable |  |  | UINT16 | 2677 | K19 | 5019
21 | GenChg | generator charging enable | bit=1Enable |  |  | UINT16 | 2678 | K20 | 5020
1 | [5 empty] | UINT16 |  | K0=5 | 5000 | Time curve voltage page setting: When the setting parameter is delivered, K0 is fixed to 5, and K1-K20 should be within the calibration range of D column. For example, if the voltage from 0 point to control time 1 is set to 50, then K1=5000; To set time curve enable (check box), K18=5; To set grid charging enable, set K19=1
2 | 4:00 | Power control time1 | 0~2359 |  |  | UINT16 | 2669 | K1 | 5001
3 | 6:00 | Power control time2 | 0~2359 |  |  | UINT16 | 2670 | K2 | 5002
4 | 10:00 | Power control time3 | 0~2359 |  |  | UINT16 | 2671 | K3 | 5003
5 | 11:00 | Power control time4 | 0~2359 |  |  | UINT16 | 2672 | K4 | 5004
6 | 14:00 | Power control time5 | 0~2359 |  |  | UINT16 | 2673 | K5 | 5005
7 | 16:00 | Power control time6 | 0~2359 |  |  | UINT16 | 2674 | K6 | 5006
8 | 20:00 | Power control time7 | 0~2359 |  |  | UINT16 | 2675 | K7 | 5007
9 | 22:00 | Power control time8 | 0~2359 |  |  | UINT16 | 2676 | K8 | 5008
10 | 50 | 0Point to control time1Voltage | 3700~6000 | 0.01 | V | UINT16 | 2711 | K9 | 5009
11 | 50 | Control time1To control time2Voltage | 3700~6000 | 0.01 | V | UINT16 | 2712 | K10 | 5010
12 | 50 | Control time2To control time3Voltage | 3700~6000 | 0.01 | V | UINT16 | 2713 | K11 | 5011
13 | 50 | Control time3To control time4Voltage | 3700~6000 | 0.01 | V | UINT16 | 2714 | K12 | 5012
14 | 50 | Control time4To control time5Voltage | 3700~6000 | 0.01 | V | UINT16 | 2715 | K13 | 5013
15 | 50 | Control time5To control time6Voltage | 3700~6000 | 0.01 | V | UINT16 | 2716 | K14 | 5014
16 | 50 | Control time6To control time7Voltage | 3700~6000 | 0.01 | V | UINT16 | 2717 | K15 | 5015
17 | 50 | Control time7To control time8Voltage | 3700~6000 | 0.01 | V | UINT16 | 2718 | K16 | 5016
18 | 50 | Control time8 to 23:59 Voltage | 3700~6000 | 0.01 | V | UINT16 | 2719 | K17 | 5017
19 | Time of Use | Time curve enable | 5=Enable,0=Disable |  |  | UINT16 | 2734 | K18 | 5018
20 | GridChg | Grid charging enable | bit0=1Enable |  |  | UINT16 | 2677 | K19 | 5019
21 | GenChg | Generator charging enable | bit0=1Enable |  |  | UINT16 | 2678 | K20 | 5020
1 | [5 empty] | UINT16 |  | K0=6 | 5000 | Time curve power page Settings: When the parameter is set, K0 is fixed to 6, and K1-K20 should be within the calibration range of D column. For example, if the power from 0 point to control time 1 is set to 12000, then K1=12000; To set time curve enable (check box), K18=5; To set grid charging enable, set K19=1
2 | 4:00 | Power control time1 | 0~2359 |  |  | UINT16 | 2669 | K1 | 5001
3 | 6:00 | Power control time2 | 0~2359 |  |  | UINT16 | 2670 | K2 | 5002
4 | 10:00 | Power control time3 | 0~2359 |  |  | UINT16 | 2671 | K3 | 5003
5 | 11:00 | Power control time4 | 0~2359 |  |  | UINT16 | 2672 | K4 | 5004
6 | 14:00 | Power control time5 | 0~2359 |  |  | UINT16 | 2673 | K5 | 5005
7 | 16:00 | Power control time6 | 0~2359 |  |  | UINT16 | 2674 | K6 | 5006
8 | 20:00 | Power control time7 | 0~2359 |  |  | UINT16 | 2675 | K7 | 5007
9 | 22:00 | Power control time8 | 0~2359 |  |  | UINT16 | 2676 | K8 | 5008
10 | 12000 | 0Point to control time1Power | 0~+14000 | 1 | W | UINT16 | 2683 | K9 | 5009
11 | 12000 | Control time1To control time2Power | 0~+14000 | 1 | W | UINT16 | 2684 | K10 | 5010
12 | 12000 | Control time2To control time3Power | 0~+14000 | 1 | W | UINT16 | 2685 | K11 | 5011
13 | 12000 | Control time3To control time4Power | 0~+14000 | 1 | W | UINT16 | 2686 | K12 | 5012
14 | 12000 | Control time4To control time5Power | 0~+14000 | 1 | W | UINT16 | 2687 | K13 | 5013
15 | 12000 | Control time5To control time6Power | 0~+14000 | 1 | W | UINT16 | 2688 | K14 | 5014
16 | 12000 | Control time6To control time7Power | 0~+14000 | 1 | W | UINT16 | 2689 | K15 | 5015
17 | 12000 | Control time7To control time8Power | 0~+14000 | 1 | W | UINT16 | 2690 | K16 | 5016
18 | 12000 | Control time8arrivetwenty three:59Power | 0~+14000 | 1 | W | UINT16 | 2691 | K17 | 5017
19 | Time of Use | Time curve enable | 5=Enable,0=Disable |  |  | UINT16 | 2734 | K18 | 5018
20 | GridChg | Grid charging enablement | bit=1Enable |  |  | UINT16 | 2677 | K19 | 5019
21 | GenChg | Generator charging enable | bit=1Enable |  |  | UINT16 | 2678 | K20 | 5020
1 | [5 empty] | UINT16 |  | K0=7 | 5000 | When the setting parameter is delivered, K0 is fixed to 7, and K1-K16 should be within the calibration range of D column. For example, if the rated inverter voltage is set to 230V, K1=2300; To set the maximum frequency of the power grid to 52Hz, K6=5200; To check the grid power limit enable, K12=80(i.e. 0x50), if the current value is read already has a value K12=5, then set the limit to K12=85(i.e. 0x55).
2 | INV V Rated | Inverter rated voltage | 2180~2320 | 0.1 | V | UINT16 | 642 | K1 | 5001
3 | Inv Hz Rated | Inverter rated frequency | 4600~5400 | 0.01 | Hz | UINT16 | 643 | K2 | 5002
4 | OnGrid A Max | Maximum on-grid current | 0~2600 | 0.01 | A | UINT16 | 644 | K3 | 5003
5 | Grid Vol Max | Maximum grid voltage | 1600~2640 | 0.1 | V | UINT16 | 645 | K4 | 5004
6 | Grid Vol Min | Minimum grid voltage | 1600~2640 | 0.1 | V | UINT16 | 646 | K5 | 5005
7 | Grid Hz Max | Maximum grid frequency | 4600~5400 | 0.01 | Hz | UINT16 | 647 | K6 | 5006
8 | Grid Hz Min | Minimum grid frequency | 4600~5400 | 0.01 | Hz | UINT16 | 648 | K7 | 5007
9 | Gen Hz Max | Maximum frequency of generator | 4600~5400 | 0.01 | Hz | UINT16 | 649 | K8 | 5008
10 | Gen Hz Min | Minimum frequency of generator | 4600~5400 | 0.01 | Hz | UINT16 | 650 | K9 | 5009
11 | Gen Vol Max | Maximum voltage of generator | 1600~2640 | 0.1 | V | UINT16 | 652 | K10 | 5010
12 | Gen Vol Min | Minimum voltage of generator | 1600~2640 | 0.1 | V | UINT16 | 653 | K11 | 5011
13 | GridLitEn | Grid power limit enable | 0xXX5X-Power limit enable 0xXX0X-Power Limit Prohibit |  |  | UINT16 | 2733 | K12 | 5012
14 | Grid Pmax kW | Maximum power of the power grid | 0-2000 | 0.1 | kW | UINT16 | 2735 | K13 | 5013
15 | CT Ratio | External current Hall ratio | 0-1000 | 1 |  | UINT16 | 708 | K14 | 5014
1 | [5 empty] | UINT16 |  | K0=8 | 5000 | When the setting parameter is delivered, K0 is fixed to 8, and K1-K15 should be within the calibration range of column D. For example, to set the interface type of the oil machine as the oil machine, K1=1; To select OnGrid Always On, K2=80(0x50), if Only Bat En is also selected, then set the limit to K2=85(0x55).
2 | GenPort Type | generator interface type | 5=Smart load 10=AC Coulpe 0=diesel generator |  |  | UINT16 | 701 | K1 | 5001
3 | OnGrid Always On | Ensure intelligent load power supply enable | 0x5=samrt all onEnable 0x50=Only Bat onEnable 0x55=Both are enabled |  |  | UINT16 | 702 | K2 | 5002
| Only Bat En | Only battery-backed smart load power supply is enabled
4 | Gen Mode | generator operation mode | 5=VFmodel 0=PQmodel |  |  | UINT16 | 705 | K3 | 5003
5 | Gen Pmax kW | External generator maximum power setting | 0-1000 | 0.1 | KW | UINT16 | 2736 | K4 | 5004
6 | Gen Signal En | Control generator signal enable | 0x5=Gen Signal EnEnable |  |  | UINT16 | 703 | K5 | 5005
7 | On Soc % | Smart load start up SOC | 40~100 | 1 | % | UINT16 | 3547 | K6 | 5006
8 | Off Soc % | Smart load shutdown SOC | 30~95 | 1 | % | UINT16 | 3548 | K7 | 5007
9 | On Vol V | Smart loadStarting voltage | 4900~6000 | 0.01 | V | UINT16 | 3549 | K8 | 5008
10 | Off Vol V | Smart loadShutdown voltage | 4800~5800 | 0.01 | V | UINT16 | 3550 | K9 | 5009
11 | Start Power | Smart load start up PV power | 100~12000 | 1 | W | UINT16 | 3551 | K10 | 5010
12 | CoupleFre Hz | Ac Couplefrequency | 5000~5500 | 0.01 | Hz | UINT16 | 707 | K11 | 5011
13 | On Soc % | Ac Couplestart upSOC | 0~80 | 1 | % | UINT16 | 3553 | K12 | 5012
14 | Off Soc % | Ac Coupleshut downSOC | 10~90 | 1 | % | UINT16 | 3554 | K13 | 5013
15 | On Vol V | Ac CoupleStarting voltage | 4000~5600 | 0.01 | V | UINT16 | 3557 | K14 | 5014
16 | Off Vol V | Ac CoupleShutdown voltage | 4200~5800 | 0.01 | V | UINT16 | 3558 | K15 | 5015
1 | [5 empty] | UINT16 |  | K0=9 | 5000 | When the parameter is set to be delivered, K0 is fixed to 9, and K1-K15 should be within the calibration range of column D. For example, to set the Sell First operating mode, K1=1; To check Solar Sell, K5=5
2 | Sell First Zero Ex To GridPort Zero Ex To CT | Power sales priority mode; Zero export to the gridport mode; Zero export to CT mode; | 1=Sell First 2=Zero Ex To GridProt 3=Zero Ex To CT Other = invalid |  |  | UINT16 | 2083 | K1 | 5001
3 | Max Sell Power W | Maximum power selling | 0-12000 | 1 | W | UINT16 | 700 | K2 | 5002
4 | Solar Sell | Photovoltaic power grid switch | 5-Enable,0-DisableOther = invalid |  |  | UINT16 | 2084 | K3 | 5003
5 | Solar Sell | Photovoltaic power grid switch | 5-Enable,0-Disableother=invalid |  |  | UINT16 | 2085 | K4 | 5004
6 | GenChgEn | Generator charging enable | 0x5-Enable diesel engine charging;0x50-Power Limit |  |  | UINT16 | 2732 | K5 | 5005
7 | GridChgEn | Grid charging enablement | 0x5-Enable grid charging;0x50-Power Limit |  |  | UINT16 | 2733 | K6 | 5006
8 | Zero Ex Power W | Maximum reverse flow power | 0~200 | 1 | W | UINT16 | 2737 | K7 | 5007
9 | BatFirstEn | battary first enable | 0xXX5X-enable 0xXX0X-disable |  |  | UINT16 | 2732 | K8 | 5008
1 | [5 empty] | UINT16 |  | K0=10 | 5000
2 | Parallel Units Total Num | Number of parallel units | 0~4 | 1 | PCS | UINT16 | 706 | K1 | 5001
3 | Inv Addr | INV communication address | 0~63odd number |  |  | UINT16 | 651 | K2 | 5002
1 | [5 empty] | UINT16 |  | K0=11 | 5000 | When the parameter is set to be delivered, K0 is fixed to 11, and K1-K3 should be within the range specified in column D. For example, if the communication mode of BMS is CAN, then K1=0;
2 | BMS COM | BMSCommunication | 0-CAN 1-RS485 |  |  | UINT16 | 10032 | K1 | 5001
3 | BMS Addr | BMS communication address | 0-120 |  |  | UINT16 | 10005 | K2 | 5002
4 | BMS Prot | BMSCommunication Protocol | 0-Felicity 1-PylonTech 2-Chisage 3-Unipower 4-Renon 5-CFE 6-PACE 7-TitanSolar 8-Voltronic 9-GsHub |  |  | UINT16 | 10004 | K3 | 5003
5 | BATShareEn | Shared battery enable | 5-Enable,0-Disable other=invalid |  |  | UINT16 | 2086 | K4 | 5004
1 | [5 empty] | UINT16 |  | K0=12 | 5000
2 | CT&Meter Sel | CT&Meter select | 0=none 1=CT 2=Meter | 1 | pcs | UINT16 | 10038 | K1 | 5001
3 | Meter Type | Meter manufacturer | bit4-bit7-manufacturer 0-Eastron 1-CHNT |  |  | UINT16 | 1555 | K2 | 5002
4 | Meter Addr | Meter address | bit0-bit3-Address |  |  | UINT16 | 1555 | K3 | 5003
[7 empty] | 读当前值 |  | 写值
1 | Reconnection Times | Grid reconnection time | 0-3600 | 1 | s | UINT16 | 670 |  | 670
2 | PeNEn | PE-N enable | 0xXX55-enable 0xXX00-prohibit |  |  | UINT16 | 665 |  | 665
3 | BatFirstEn | battery first enable | 0xXX5X-enable，0xXX0X-prohibit |  |  | UINT16 | 2732 |  | 2732
4 | AcPeakShavingEn | AC peak shaving enable | 0xX1XX-enable，0xX0XX-prohibit |  |  | UINT16 | 2733 |  | 2733
5 | CT&Meter Sel | CT&Meter select | 0=none 1=CT 2=Meter | 1 | pcs | UINT16 | 10038 |  | 10038
6 | Meter Type | Meter manufacturer | bit4-bit7-manufacturer 0-Eastron 1-CHNT |  |  | UINT16 | 1555 |  | 1555
7 | Meter Addr | Meter address | bit0-bit3-Address |  |  | UINT16 | 1555 |  | 1555

## Debug Group Data
Inverter debugging group data and status
Order | Register Address | Data Type | What the data means | Number of bytes | R/W | unit | Remark
0x03 | 4000 | Group 3state0 |  |  |  |  | For debugging
0x03 | 4001 | Group 3state1
0x03 | 4002 | Group 3state2
0x03 | 4003 | Group 3state3
0x03 | 4004 | Group 3state4
0x03 | 4005 | Group 3state5
0x03 | 4006 | Group 3 Data 0 |  |  |  |  | For debugging
0x03 | 4007 | Group 3 Data 1
0x03 | 4008 | Group 3 Data 2
0x03 | 4009 | Group 3 Data 3
0x03 | 4010 | Group 3 Data 4
0x03 | 4011 | Group 3 Data 5
0x03 | 4012 | Group 3 Data 6
0x03 | 4013 | Group 3 Data 7
0x03 | 4014 | Group 3 Data 8
0x03 | 4015 | Group 3 Data 9
0x03 | 4016 | Group 3 data 10
0x03 | 4017 | Group 3 Data 11
0x03 | 4018 | Group 3 data 12
0x03 | 4019 | Group 3 data 13
0x03 | 4020 | Group 3 data 14
0x03 | 4021 | Group 3 data 15
0x03 | 4022 | Group 3 data 16
0x03 | 4023 | Group 3 data 17
0x03 | 4024 | Group 3 data 18
0x03 | 4025 | Group 3 data 19
0x03 | 4026 | Group 3 data 20
0x03 | 4027 | Group 3 Data 21
0x03 | 4028 | Group 3 data 22
0x03 | 4029 | Group 3 data 23
0x03 | 4030 | Group 3 data 24
0x03 | 4031 | Group 3 data 25
0x03 | 4032 | Group 3 data 26
0x03 | 4033 | Group 3 data 27
0x03 | 4034 | Group 3 data 28
0x03 | 4035 | Group 3 data 29
0x03 | 4036 | Group 3 data 30
0x03 | 4037 | Group 3 Data 31
DCDC debugging group data and status
Order | Register Address | Data Type | What the data means | Number of bytes | R/W | unit | Remark
0x03 | 4500 | Group 3state0 |  |  |  |  | For debugging
0x03 | 4501 | Group 3state1
0x03 | 4502 | Group 3state2
0x03 | 4503 | Group 3state3
0x03 | 4504 | Group 3state4
0x03 | 4505 | Group 3state5
0x03 | 4506 | Group 3 Data 0 |  |  |  |  | For debugging
0x03 | 4507 | Group 3 Data 1
0x03 | 4508 | Group 3 Data 2
0x03 | 4509 | Group 3 Data 3
0x03 | 4510 | Group 3 Data 4
0x03 | 4511 | Group 3 Data 5
0x03 | 4512 | Group 3 Data 6
0x03 | 4513 | Group 3 Data 7
0x03 | 4514 | Group 3 Data 8
0x03 | 4515 | Group 3 Data 9
0x03 | 4516 | Group 3 data 10
0x03 | 4517 | Group 3 Data 11
0x03 | 4518 | Group 3 data 12
0x03 | 4519 | Group 3 data 13
0x03 | 4520 | Group 3 data 14
0x03 | 4521 | Group 3 data 15
0x03 | 4522 | Group 3 data 16
0x03 | 4523 | Group 3 data 17
0x03 | 4524 | Group 3 data 18
0x03 | 4525 | Group 3 data 19
0x03 | 4526 | Group 3 data 20
0x03 | 4527 | Group 3 Data 21
0x03 | 4528 | Group 3 data 22
0x03 | 4529 | Group 3 data 23
0x03 | 4530 | Group 3 data 24
0x03 | 4531 | Group 3 data 25
0x03 | 4532 | Group 3 data 26
0x03 | 4533 | Group 3 data 27
0x03 | 4534 | Group 3 data 28
0x03 | 4535 | Group 3 data 29
0x03 | 4536 | Group 3 data 30
0x03 | 4537 | Group 3 Data 31
BMS commissioning group
0x03 | 3650 | Data0 | Battery voltage |  |  |  | BMS Debugging
0x03 | 3651 | Data 1 | Battery Current
0x03 | 3652 | Data 2 | SOC |  |  | 1
0x03 | 3653 | Data 3 | Charging voltage |  |  | 0.1
0x03 | 3654 | Data 4 | Discharge voltage |  |  | 0.1
0x03 | 3655 | Data 5 | Charge limiting current |  |  | 0.1
0x03 | 3656 | Data 6 | Discharge limiting current |  |  | 0.1
0x03 | 3657 | Data 7 | state
0x03 | 3658 | Data 8
0x03 | 3659 | Data 9
0x03 | 3660 | Data 10 | temperature |  |  | 0.1

## Historical data
History
| Order | Register Address | Data Type | What the data means | Read and Write | byte | Remark
|  | 4998 | short | History Page | Read and Write |  | 0-100
| 0x03 | 4999 | short | Total number of records | Read and Write | 2 | 0-1000
Record 1 | 0x03 | 5000 | short | years and months | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5001 | short | Date and hour | Read-only | 2 | The high byte is the date and the low byte is the hour
| 0x03 | 5002 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5003 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 2 | 0x03 | 5004 | short | years and months | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5005 | short | Date and hour | Read-only | 2 | The high byte is the date and the low byte is the hour
| 0x03 | 5006 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5007 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 3 | 0x03 | 5008 | short | years and months | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5009 | short | Date and hour | Read-only | 2 | The high byte is the date and the low byte is the hour
| 0x03 | 5010 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5011 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 4 | 0x03 | 5012 | short | years and months | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5013 | short | Date and hour | Read-only | 2 | The high byte is the date and the low byte is the hour
| 0x03 | 5014 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5015 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 5 | 0x03 | 5016 | short | years and months | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5017 | short | Date and hour | Read-only | 2 | The high byte is the date and the low byte is the hour
| 0x03 | 5018 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5019 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 6 | 0x03 | 5020 | short | years and months | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5021 | short | Date and hour | Read-only | 2 | The high byte is the date and the low byte is the hour
| 0x03 | 5022 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5023 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 7 | 0x03 | 5024 | short | years and months | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5025 | short | Date and hour | Read-only | 2 | The high byte is the date and the low byte is the hour
| 0x03 | 5026 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5027 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 8 | 0x03 | 5028 | short | years and months | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5029 | short | Date and hour | Read-only | 2 | The high byte is the date and the low byte is the hour
| 0x03 | 5030 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5031 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 9 | 0x03 | 5032 | short | years and months | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5033 | short | Date and hour | Read-only | 2 | The high byte is the date and the low byte is the hour
| 0x03 | 5034 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5035 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 10 | 0x03 | 5036 | short | years and months | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5037 | short | Date and hour | Read-only | 2 | The high byte is the date and the low byte is the hour
| 0x03 | 5038 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5039 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code

## Fault information table
Register Address | Status word | Bit0~Bit15 | Indicates the information content (1: its status is valid; 0: its status is invalid) |  | coding
|  |  | English | Description |  | Table 8-1 W0 |  |  | Table 8-1 W0 |  | 表8-2 W2
2061 | Alarm status word1 | Bit00 | Insulation_Warning | Insulation impedance too low alarm | W01 | bit15 |  |  | bit15 | BMS communication abnormality | bit15
|  | Bit01 | Comm_LCD_Lose_Warning | LCDCommunication disconnection alarm between the screen and the control board | W02 | bit14 |  |  | bit14 |  | bit14
|  | Bit02 | LVRT_Fault_Warning | Low voltage ride-through fault alarm | W03 | bit13 | Grid underfrequency abnormality |  | bit13 |  | bit13
|  | Bit03 | Fan_Faullt_Warning | Fan failure alarm | W04 | bit12 | Fan failure |  | bit12 | Fan failure | bit12
|  | Bit04 | PV1 low voltage warning | PV 1 voltage alarm | W05 | bit11 | Generator frequency abnormality |  | bit11 |  | bit11
|  | Bit05 | PV2 low voltage warning | PV 2 voltage alarm | W06 | bit10 | Abnormal generator amplitude |  | bit10 | Photovoltaic 2 overvoltage | bit10 | 1: Meter communication is normal
|  | Bit06 | Battaey No voltage warning | Battery low voltage warning | W07 | bit9 | Grid overfrequency abnormality |  | bit9 | Photovoltaic 1 overvoltage | bit9 | 1: Display communication normal
|  | Bit07 | Grid No Voltage warning | Grid power failure warning | W08 | bit8 | Grid overvoltage abnormality |  | bit8 | Battery overvoltage | bit8 | 1: Debugging communication normal
|  | Bit08 | Gen No Voltage warning | Generator power failure warning | W09 | bit7 | Grid undervoltage abnormality |  | bit7 |  | bit7
|  | Bit09 | AC_Volt_Unbalance_Warning | AC three-phase voltage unbalanceFault alarm | W10 | bit6 | Load low voltage |  | bit6 |  | bit6
|  | Bit10 | AC_PLL_Warning | AC PLL failed | W11 | bit5 | Phase lock failed |  | bit5 |  | bit5
|  | Bit11 | Power_Derate_ Warning | Derating alarm | W12 | bit4 | Temperature resistor not connected |  | bit4 | Temperature resistor not connected | bit4
|  | Bit12 | Reseverd | Reserve | W13 | bit3 | The phase sequence of the generator is wrong | E | bit3 | Low battery | bit3
|  | Bit13 | Heatsink_LoTemp_Warning | IGBT Radiator temperature low alarm | W14 | bit2 | The grid phase sequence is wrong |  | bit2 | Photovoltaic 2 low voltage | bit2
|  | Bit14 | BMSCommunication Warning | BMS communication disconnection alarm | W15 | bit1 | The generator is out of power |  | bit1 | Photovoltaic 1 low voltage | bit1
|  | Bit15 | Grid High_Voltage Warning | AC grid overvoltage alarm | W16 | bit0 | The grid is out of power |  | bit0 | Battery low voltage | bit0
2062 | Alarm status word2 | Bit00 | Grid PhaseSeque_Fault | AC grid phase sequence error | W17
|  | Bit01 | Grid High_Freq Warning | AC power grid over frequency alarm | W18 | Table 8-3 F0 |  |  | Table 8-3 F0
|  | Bit02 | Gen_Volt_Warning | Generator AC over-voltage or under-voltage alarm | W19 | bit15 |  |  | bit15
|  | Bit03 | Gen PhaseSeque_Fault | The AC phase sequence of the generator is wrong | W20 | bit14 |  |  | bit14
|  | Bit04 | Gen_Freq_Warning | Diesel generator over-frequency and under-frequency alarm | W21 | bit13 |  |  | bit13
|  | Bit05 | Reseverd | Reserve | W22 | bit12 |  |  | bit12
|  | Bit06 | Loadlow voltage warning | Load low voltage | W23 | bit11 |  |  | bit11
|  | Bit07 | PV2_VoltHigh_warning | Photovoltaic 2 overvoltage | W24 | bit10 | DC BUS voltage abnormal |  | bit10 | DC bus undervoltage
|  | Bit08 | PV1_VoltHigh_warning | Photovoltaic 1 overvoltage | W25 | bit9 |  |  | bit9 | Insulation resistance is too large
[6 empty] | bit8 |  |  | bit8 | Leakage current is too large
|  | Bit09 | Bat_VoltHigh_warning | Battery overvoltage | W26 | bit7 | IGBT Failure |  | bit7
|  | Bit10 | Bat SOC Low warning | Low battery | W27 | bit6 |  |  | bit6
|  | Bit11 | Reseverd | Reserve | W28 | bit5 |  |  | bit5
|  | Bit12 | Reseverd | Reserve | W29 | bit4 | Over temperature |  | bit4 | Over temperature
|  | Bit13 | Comm_Meter_Lose_Warning | The meter communication is abnormal | W30 | bit3 | Hardware overcurrent |  | bit3 | DC hardware overcurrent
|  | Bit14 | Grid Low_Voltage Warning | AC grid undervoltage alarm | W31 | bit2 | Software overcurrent |  | bit2 | DC software overcurrent
|  | Bit15 | Grid Low_Freq Warning | AC grid underfrequency alarm | W32 | bit1 | DC overvoltage |  | bit1 | DC bus overvoltage
[6 empty] | bit0 | Load overvoltage or undervoltage |  | bit0 | Reverse battery connection
Register Address | Status word | Bit0~Bit15 | Indicates the information content (1: its status is valid; 0: its status is invalid) |  | Coding
|  |  | English | Description |  | Table 8-4 F1 |  |  | Table 8-4 F1
2063 | Fault status word1 | Bit00 | DC Inversed Failure | Battery polarity reverse connection fault | F01 | bit15 |  |  | bit15
|  | Bit01 | Insulattion_Failure | Permanent insulation resistance failure | F02 | bit14 |  |  | bit14
|  | Bit02 | EEPROM_Read_Failure | Read memory error | F03 | bit13 |  |  | bit13
|  | Bit03 | EEPROM_Write_Failure | Write memory error | F04 | bit12 |  |  | bit12
|  | Bit04 | DC soft startFailure | Battery slow start failed | F05 | bit11 |  |  | bit11
|  | Bit05 | Tz_Dc_OverCurr_Fault | DC hardware overcurrent | F06 | bit10 |  |  | bit10
|  | Bit06 | DC_OverCurr_Failure | DC software overcurrent fault | F07 | bit9 |  |  | bit9
|  | Bit07 | AuxPowerBoard_Failure | Auxiliary switch power supply failure (auxiliary switch power supply | F08 | bit8 |  |  | bit8
|  | Bit08 | IGBT_Failure | IGBTFault | F09 | bit7 |  |  | bit7
|  | Bit09 | Reseverd | Reserve | F10 | bit6 |  |  | bit6
|  | Bit10 | AC_Main Contactor_Failure | AC main contactor error | F11 | bit5 |  |  | bit5
|  | Bit11 | AC_Slave Contactor_Failure | AC auxiliary contactor error | F12 | bit4 |  |  | bit4
|  | Bit12 | Tz_Ac_OverCurr_Fault | Hardware AC overcurrent fault | F13 | bit3 |  |  | bit3
|  | Bit13 | AC_OverCurr_Failure | AC software overcurrent fault | F14 | bit2 |  |  | bit2
|  | Bit14 | GFCI_Failure | GFCI (RCD)AC leakage current fault | F15 | bit1 |  |  | bit1 | Photovoltaic 2 reverse connection
|  | Bit15 | Tz_COM_OC_Fault | Three-phase current and overcurrent fault | F16 | bit0 |  |  | bit0 | Photovoltaic 1 reverse connection
2064 | Fault status word 2 | Bit00 | BusUnbalance_Fault | DC bus unbalance fault | F17
|  | Bit01 | Load_voltage_Fault | Load overvoltage or undervoltage | F18
|  | Bit02 | Reseverd | Reserve | F19
|  | Bit03 | Reseverd | Reserve | F20
|  | Bit04 | Reseverd | Reserve | F21
|  | Bit05 | Reseverd | Reserve | F22
|  | Bit06 | BUS VoltLow Fault | The DC bus voltage is too low | F23
|  | Bit07 | Grid_Overload_Fault | Grid current overload | F24
|  | Bit08 | Gen_Overload_Fault | Generator AC current overload | F25
|  | Bit09 | BUS_VoltHigh_Fault | DC bus voltage is too high | F26
|  | Bit10 | BUS_Voltage_Fault | DC bus voltage is abnormal | F27
|  | Bit11 | AC_BackFeed_Fault | AC backflow fault | F28
|  | Bit12 | Heatsink_HiTemp_Fault | IGBT Radiator temperature is too high | F29
|  | Bit13 | PV1 Inversed Failure | PV arc fault | F30
|  | Bit14 | PV1 Inversed Failure | Photovoltaic1Reverse connection fault | F31
|  | Bit15 | PV2Inversed Failure | Photovoltaic2Reverse connection fault | F32

## Program Upgrade
Register | Signal name | Number of bytes | Type | Read and Write | Remark
10000-10003 | Manufacturer | 8 | String | RO | ZWGK
10004 | BMS Communication Protocol | 2 | UINT16 | RW | 0-Felicity 1-Pylon 2-Chisage 3-Unipower 4-Renon 5-CFE
10005 | BMS Address | 2 | UINT16 | RW | 1-255
10006 | BMS battery PACK quantity | 2 | UINT16 | RW | 1~16
10007 | Equ Days | 2 | UINT16 | RW | 1-100
10008-10023 | Model name | 32 | String | RO | PVESS-M12K-FA220-DD48
10024-10031 | Serial number | 16 | String | RO | Z2012KAK8250001
10032 | BMS communication method | 2 | UINT16 | RW | 0-CAN 1-RS485
10033 | WIFI upgrade baud rate | 2 | UINT16 | RW | 96-9600 192-19200 1152-15200 Others indicate 115200
10034 | INV Software version | 2 | UINT16 | RO | 0X1123 means V1.1.2.3
10035 | DCDC Software version | 2 | UINT16 | RO | 0X1123 means V1.1.2.3
10036 | HIMI software version | 2 | UINT16 | RO | 0X1123 means V1.1.2.3
10037 | Protocol version | 2 | UINT16 | RO | 0X1123 means V1.1.2.3
10038 | Electric meter CT selection | 2 | UINT16 | RW | 0-None 1-CT 2-METER
10039 | Language | 2 | UINT16 | RW | 0-EN 1-DE 6-CN
13400-13463 | Online upgrade configuration-file name | 128 | String | RW
13480-13482 | Online upgrade configuration-File modification time | 6 | MLB |  | 1, in the upgrade package file properties“File modification time”. 2, Format: Year/month/date/hour/minute/Second
13483-13485 | Upgrade Data Pack-File modification time | 6 | MLB | RW
13486-13487 | Upgrade Data Pack-Large file size | 4 | UINT32 | RW | File size
13488 | Upgrade Data Pack-Total Frames | 2 | UINT16 | RW
13489 | Upgrade Data Pack-Current frame number | 2 | UINT16 | RW
13490-13589 | Upgrade Data Pack-Data Bytes1-100 | 200 | String | RW | 200Bytes, the last frame is not enough and is padded with zeros.
13590 | Online upgrade status | 2 | UINT16 | RO | 0-Not upgraded;1-The upgrade package is downloading; 2-Download completed, upgrading; 3-Upgrade successful; 4-Upgrade failed;
13591-13640 | Online upgrade received frame number1-50 | 2*50 | UINT16 | RO | The number of the received packet, start from 1
13641 | Online upgrade percentage | 2 | UINT16 | RO | 1%

## Debug Data
Inverter
Order | Register Address | Data Type | What the data means | Number of bytes | R/W | unit |  | Remark | Table 8-1 W0 |  |  | Table 9-1 W0
0x03 | 1984 | Group 3 Data 0 | [5 empty] | For debugging | bit15 |  |  | bit15 | BMS communication abnormality
0x03 | 1985 | Group 3 Data 1 | [6 empty] | bit14 |  |  | bit14
0x03 | 1986 | Group 3 Data 2 | [6 empty] | bit13 |  |  | bit13
0x03 | 1987 | Group 3 Data 3 | [6 empty] | bit12 | Fan failure |  | bit12 | Fan failure
0x03 | 1988 | Group 3 Data 4 | [6 empty] | bit11 | generator frequency abnormality |  | bit11
0x03 | 1989 | Group 3 Data 5 | [6 empty] | bit10 | Abnormal generator amplitude |  | bit10 | Photovoltaic 2 overvoltage
0x03 | 1990 | Group 3 Data 6 | [6 empty] | bit9 | Abnormal grid frequency |  | bit9 | Photovoltaic 1 overvoltage
0x03 | 1991 | Group 3 Data 7 | [6 empty] | bit8 | Abnormal power grid amplitude |  | bit8 | Battery overvoltage
0x03 | 1992 | Group 3 Data 8 | [6 empty] | bit7 |  |  | bit7
0x03 | 1993 | Group 3 Data 9 | [6 empty] | bit6 | Load low voltage |  | bit6
0x03 | 1994 | Group 3 data 10 | [6 empty] | bit5 | Phase lock failed |  | bit5
0x03 | 1995 | Group 3 Data 11 | [6 empty] | bit4 | Temperature resistor not connected |  | bit4 | Temperature resistor not connected
0x03 | 1996 | Group 3 data 12 | [6 empty] | bit3 | The phase sequence of the generator is wrong | E | bit3
0x03 | 1997 | Group 3 data 13 | [6 empty] | bit2 | The grid phase sequence is wrong |  | bit2 | Photovoltaic 2 low voltage
0x03 | 1998 | Group 3 data 14 | [6 empty] | bit1 | generator low voltage |  | bit1 | Photovoltaic 1 low voltage
0x03 | 1999 | Group 3 data 15 | [6 empty] | bit0 | Grid low voltage |  | bit0 | Battery low voltage
0x03 | 2000 | Group 3 data 16
0x03 | 2001 | Group 3 data 17 | [6 empty] | Table 8-3 F0 |  |  | Table 9-3 F0
0x03 | 2002 | Group 3 data 18 | [6 empty] | bit15 |  |  | bit15
0x03 | 2003 | Group 3 data 19 | [6 empty] | bit14 |  |  | bit14
0x03 | 2004 | Group 3 data 20 | [6 empty] | bit13 |  |  | bit13
0x03 | 2005 | Group 3 Data 21 | [6 empty] | bit12 |  |  | bit12
0x03 | 2006 | Group 3 data 22 | [6 empty] | bit11 |  |  | bit11
0x03 | 2007 | Group 3 data 23 | [6 empty] | bit10 | DC undervoltage |  | bit10 | DC bus undervoltage
0x03 | 2008 | Group 3 data 24 | [6 empty] | bit9 |  |  | bit9 | Insulation resistance is too large
0x03 | 2009 | Group 3 data 25 | [6 empty] | bit8 |  |  | bit8 | Leakage current is too large
0x03 | 2010 | Group 3 data 26 | [6 empty] | bit7 | IGBT Failure |  | bit7
0x03 | 2011 | Group 3 data 27 | [6 empty] | bit6 |  |  | bit6
0x03 | 2012 | Group 3 data 28 | [6 empty] | bit5 |  |  | bit5
0x03 | 2013 | Group 3 data 29 | [6 empty] | bit4 | Over temperature |  | bit4 | Over temperature
0x03 | 2014 | Group 3 data 30 | [6 empty] | bit3 | Hardware overcurrent |  | bit3 | DC hardware overcurrent
0x03 | 2015 | Group 3 Data 31 | [6 empty] | bit2 | Software overcurrent |  | bit2 | DC software overcurrent
0x03 | 2016 | Group 2state0 | Alarm status 0 |  |  |  | Table 8-1 | W0 | bit1 | DC overvoltage |  | bit1 | DC bus overvoltage
0x03 | 2017 | Group 2state1 | Alarm status 1 |  |  |  | Table 8-2 | W1 | bit0 | Load overvoltage or undervoltage |  | bit0 | Reverse battery connection
0x03 | 2018 | Group 2state2 | Alarm status 1 |  |  |  | Table 8-3 | W2
0x03 | 2019 | Group 2state3 | Fault state 0 |  |  |  | Table 8-3 | F0 | Table 8-4 F1 |  |  | Table 9-4 F1
0x03 | 2020 | Group 2state4 | Fault state 1 |  |  |  | Table 8-4 | F1 | bit15 |  |  | bit15
0x03 | 2021 | Group 2state5 | Fault state 2 |  |  |  | Table 8-5 | F2 | bit14 |  |  | bit14
0x03 | 2022 | Group 3state0 | [5 empty] | For debugging | bit13 |  |  | bit13
0x03 | 2023 | Group 3state1 | [6 empty] | bit12 |  |  | bit12
0x03 | 2024 | Group 3state2 | [6 empty] | bit11 |  |  | bit11
0x03 | 2025 | Group 3state3 | [6 empty] | bit10 |  |  | bit10
0x03 | 2026 | Group 3state4 | [6 empty] | bit9 |  |  | bit9
0x03 | 2027 | Group 3state5 | [6 empty] | bit8 |  |  | bit8
DCDC | [8 empty] | bit7 |  |  | bit7
Order | Register Address | Data Type | What the data means | Number of bytes | R/W | unit |  | Remark | bit6 |  |  | bit6
0x03 | 1984 | Group 3 Data 0 | [5 empty] | For debugging | bit5 |  |  | bit5
0x03 | 1985 | Group 3 Data 1 | [6 empty] | bit4 |  |  | bit4
0x03 | 1986 | Group 3 Data 2 | [6 empty] | bit3 |  |  | bit3
0x03 | 1987 | Group 3 Data 3 | [6 empty] | bit2 |  |  | bit2
0x03 | 1988 | Group 3 Data 4 | [6 empty] | bit1 |  |  | bit1 | Photovoltaic 2 reverse connection
0x03 | 1989 | Group 3 Data 5 | [6 empty] | bit0 |  |  | bit0 | Photovoltaic 1 reverse connection
0x03 | 1990 | Group 3 Data 6
0x03 | 1991 | Group 3 Data 7
0x03 | 1992 | Group 3 Data 8
0x03 | 1993 | Group 3 Data 9
0x03 | 1994 | Group 3 data 10
0x03 | 1995 | Group 3 Data 11
0x03 | 1996 | Group 3 data 12
0x03 | 1997 | Group 3 data 13
0x03 | 1998 | Group 3 data 14
0x03 | 1999 | Group 3 data 15
0x03 | 2000 | Group 3 data 16
0x03 | 2001 | Group 3 data 17
0x03 | 2002 | Group 3 data 18
0x03 | 2003 | Group 3 data 19
0x03 | 2004 | Group 3 data 20
0x03 | 2005 | Group 3 Data 21
0x03 | 2006 | Group 3 data 22
0x03 | 2007 | Group 3 data 23
0x03 | 2008 | Group 3 data 24
0x03 | 2009 | Group 3 data 25
0x03 | 2010 | Group 3 data 26
0x03 | 2011 | Group 3 data 27
0x03 | 2012 | Group 3 data 28
0x03 | 2013 | Group 3 data 29
0x03 | 2014 | Group 3 data 30
0x03 | 2015 | Group 3 Data 31
0x03 | 2016 | Group 2state0 | Alarm status 0 |  |  |  | Table 9-1 | W0
0x03 | 2017 | Group 2state1 | Alarm status 1 |  |  |  | Table 9-2 | W1
0x03 | 2018 | Group 2state2
0x03 | 2019 | Group 2state3 | Fault state 0 |  |  |  | Table 9-3 | F0
0x03 | 2020 | Group 2state4 | Fault state 1 |  |  |  | Table 9-4 | F1
0x03 | 2021 | Group 2state5 | Fault state 2 |  |  |  | Table 9-5 | F2
0x03 | 2022 | Group 3state0 | [5 empty] | For debugging
0x03 | 2023 | Group 3state1
0x03 | 2024 | Group 3state2
0x03 | 2025 | Group 3state3
0x03 | 2026 | Group 3state4
0x03 | 2027 | Group 3state5

## Sheet2
INVERTER
Order | Register address | Data type | Data meaning | Number of bytes | R/W | UNIT |  | Remark
0x03 | 1952 | group2data0
0x03 | 1953 | group2data1
0x03 | 1954 | group2data2
0x03 | 1955 | group2data3
0x03 | 1956 | group2data4
0x03 | 1957 | group2data5
0x03 | 1958 | group2data6
0x03 | 1959 | group2data7
0x03 | 1960 | group2data8
0x03 | 1961 | group2data9
0x03 | 1962 | group2data10
0x03 | 1963 | group2data11
0x03 | 1964 | group2data12
0x03 | 1965 | group2data13
0x03 | 1966 | group2data14
0x03 | 1967 | group2data15
0x03 | 1968 | group2data16
0x03 | 1969 | group2data17
0x03 | 1970 | group2data18
0x03 | 1971 | group2data19
0x03 | 1972 | group2data20
0x03 | 1973 | group2data21
0x03 | 1974 | group2data22
0x03 | 1975 | group2data23
0x03 | 1976 | group2data24
0x03 | 1977 | group2data25
0x03 | 1978 | group2data26
0x03 | 1979 | group2data27
0x03 | 1980 | group2data28
0x03 | 1981 | group2data29
0x03 | 1982 | group2data30 | FPGA version number
0x03 | 1983 | group2data31 | system capacity
0x03 | 1984 | group3data0 | [5 empty] | for debugging
0x03 | 1985 | group3data1
0x03 | 1986 | group3data2
0x03 | 1987 | group3data3
0x03 | 1988 | group3data4
0x03 | 1989 | group3data5
0x03 | 1990 | group3data6
0x03 | 1991 | group3data7
0x03 | 1992 | group3data8
0x03 | 1993 | group3data9
0x03 | 1994 | group3data10
0x03 | 1995 | group3data11
0x03 | 1996 | group3data12
0x03 | 1997 | group3data13
0x03 | 1998 | group3data14
0x03 | 1999 | group3data15
0x03 | 2000 | group3data16
0x03 | 2001 | group3data17
0x03 | 2002 | group3data18
0x03 | 2003 | group3data19
0x03 | 2004 | group3data20
0x03 | 2005 | group3data21
0x03 | 2006 | group3data22
0x03 | 2007 | group3data23
0x03 | 2008 | group3data24
0x03 | 2009 | group3data25
0x03 | 2010 | group3data26
0x03 | 2011 | group3data27
0x03 | 2012 | group3data28
0x03 | 2013 | group3data29
0x03 | 2014 | group3data30
0x03 | 2015 | group3data31
0x03 | 2016 | group2state0 | alarm0 |  |  |  | table8-1 | W0
0x03 | 2017 | group2state1 | alarm1 |  |  |  | table8-2 | W1
0x03 | 2018 | group2state2 | alarm1 |  |  |  | table8-3 | W2
0x03 | 2019 | group2state3 | fault0 |  |  |  | table8-3 | F0
0x03 | 2020 | group2state4 | fault1 |  |  |  | table8-4 | F1
0x03 | 2021 | group2state5 | fault2 |  |  |  | table8-5 | F2
0x03 | 2022 | group3state0 | [5 empty] | for debugging
0x03 | 2023 | group3state1
0x03 | 2024 | group3state2
0x03 | 2025 | group3state3
0x03 | 2026 | group3state4
0x03 | 2027 | group3state5
DCDC
Order | Register address | Data type | Data meaning | Number of bytes | R/W | UNIT |  | Remark
0x03 | 1984 | group3data0 | [5 empty] | for debugging
0x03 | 1985 | group3data1
0x03 | 1986 | group3data2
0x03 | 1987 | group3data3
0x03 | 1988 | group3data4
0x03 | 1989 | group3data5
0x03 | 1990 | group3data6
0x03 | 1991 | group3data7
0x03 | 1992 | group3data8
0x03 | 1993 | group3data9
0x03 | 1994 | group3data10
0x03 | 1995 | group3data11
0x03 | 1996 | group3data12
0x03 | 1997 | group3data13
0x03 | 1998 | group3data14
0x03 | 1999 | group3data15
0x03 | 2000 | group3data16
0x03 | 2001 | group3data17
0x03 | 2002 | group3data18
0x03 | 2003 | group3data19
0x03 | 2004 | group3data20
0x03 | 2005 | group3data21
0x03 | 2006 | group3data22
0x03 | 2007 | group3data23
0x03 | 2008 | group3data24
0x03 | 2009 | group3data25
0x03 | 2010 | group3data26
0x03 | 2011 | group3data27
0x03 | 2012 | group3data28
0x03 | 2013 | group3data29
0x03 | 2014 | group3data30
0x03 | 2015 | group3data31
0x03 | 2016 | group2state0 | alarm0 |  |  |  | table9-1 | W0
0x03 | 2017 | group2state1 | alarm1 |  |  |  | table9-2 | W1
0x03 | 2018 | group2state2
0x03 | 2019 | group2state3 | fault0 |  |  |  | table9-3 | F0
0x03 | 2020 | group2state4 | fault1 |  |  |  | table9-4 | F1
0x03 | 2021 | group2state5 | fault2 |  |  |  | table9-5 | F2
0x03 | 2022 | group3state0 | [5 empty] | for debugging
0x03 | 2023 | group3state1
0x03 | 2024 | group3state2
0x03 | 2025 | group3state3
0x03 | 2026 | group3state4
0x03 | 2027 | group3state5

## Sheet1
English | EN
German | DE
Italian | IT
Spanish | ES
Portuguese | PT
French | FR | 0x0000 | samrt all on | Only Bat on
Chinese | CN | 0x0005 | samrt all on | Only Bat on
|  | 0x0050 | samrt all on | Only Bat on
|  | 0x0055 | samrt all on | Only Bat on